| Credit Requirement: |  |  | Maximum 20 credits can be achieved based on the following upgrades in the last 3 years: i. 8 credits for replacing at least 30% by total cooling capacity serving the building from air-cooled chiller to either water-cooled chiller or oil free variable speed air/ water cooled chiller; ii. 6 credits for at least 50% by total cooling capacity serving the building are high efficiency chiller (>15% higher than BEC 2012’s COP at full load in the same category); iii. 6 credits for at least 80% by total cooling capacity of all VRF are high efficiency VRF (>15% higher than BEC 2012’s COP at full load in the same category); iv. 4 credits for at least 50% of total fresh air flow rate to the building are controlled by CO2 sensors; v. 3 credits for at least 50% of air conditioned areas not frequently used (e.g. meeting room, conference room, etc.) are served by air conditioning with motion sensors controlling its operation; vi. 4 credits for at least 30% of total fresh air flow rate to the building are pre-treated by heat recovery system; vii. 4 credits for at least 30% of air conditioned areas are served by enthalpy controlled free cooling; viii. 4 credits for at least 50% of total supply air flow rate of all PAU/ AHU are supplied by VSD fans; ix. 4 credits for at least 50% of total supply air flow rate of all FCU are supplied by VSD fans; x. 4 credits for at least 50% of total chilled water flow rate of all chilled water pumps are VSD driven; xi. 4 credits for at least 50% of total condensing water flow rate of all condensing water pumps are VSD driven; xii. 3 credits for having "automatic tube cleaning systems" on all water-cooled chillers; xiii. 4 credits for electronic ballasts for all fluorescent lamps; xiv. 4 credits for replacing >80% of T8 to T5; xv. 4 credits for at least 30% of all areas are served by LED lighting; xvi. 3 credits for at least 30% of all public areas such as corridors, toilets, etc. are served by lighting with motion/ occupancy sensor controls; xvii. 3 credits for at least 30% of all areas accessible to daylight are served by lighting with dimming controls to adjust lighting level to suit the space's need; xviii. 2 credits for having separate lighting controls for the window perimeter and that for the interior. Lighting at the window perimeter can be turned down or off on a sunny day; xix. 5 credits for at least 50% of all window areas with direct access to daylight are applied with solar window film (i.e. windows that are heavily shaded or not having a direct view to the sky are excluded); xx. 3 credits for at least 30% of all lift motor power are re-generative lift; xxi. 1 credit for at least 30% of all lift motor power are Variable Voltage Variable Frequency (VVVF) drives and/or direct current motor controlled by solid-state elements for lifts; xxii. 1 credit for at least 30% of all escalator motor power are VVVF drive systems and high gear systems for escalators; xxiii. 1 credit for at least 30% of all escalator motor power are controlled by optical sensors to allow escalators to be stopped or slowed down when there are no users; xxiv. 1 credit for at least 50% of all lift (by quantity) have automatic switch off lighting and ventilation fan inside the lift car when the lift is in standby/ idle mode; xxv. 2 credits for adding harmonics filter to reduce total harmonics distortion (THD) in electricity distribution system; xxvi. 1 credit for having heat pump pre-heating at least 50% of domestic hot water (by quantity of sanitary fitting); xxvii. 1 credit for having thermostat on/off and/or speed control for exhaust fans serving at least 50% of plant rooms area but exclude those rooms that require continuous exhaust due to health and safety issues (e.g. chemical storage room, refuse storage room); and xxviii. 1 credit for openable windows for mixed mode/ natural ventilation. |  |  |
| --- | --- | --- | --- | --- | --- |
| Credit Attainable: |  |  |  | 20 |  |
| Credit(s) anticipated for this submission: |  |  |  |  |  |
| Checklist: |  |  |  |  |  |
| The following upgrade(s) is/are implemented in the last 3 years: |  |  |  |  |  |
| ☐ |  | Replacing at least 30% by total cooling capacity serving the building from air-cooled chiller to either water-cooled chiller or oil free variable speed air/ water cooled chiller; |  |  |  |
| ☐ |  | At least 50% by total cooling capacity serving the building are high efficiency chiller (>15% higher than BEC 2012’s COP at full load in the same category); |  |  |  |
| ☐ |  | At least 80% by total cooling capacity of all VRF are high efficiency VRF (>15% higher than BEC 2012’s COP at full load in the same category); |  |  |  |
| ☐ |  | At least 50% of total fresh air flow rate to the building are controlled by CO2 sensors; |  |  |  |
| ☐ |  | At least 50% of air conditioned areas not frequently used (e.g. meeting room, conference room, etc.) are served by air conditioning with motion sensors controlling its operation; |  |  |  |
| ☐ |  | At least 30% of total fresh air flow rate to the building are pre-treated by heat recovery system; |  |  |  |
| ☐ |  | At least 30% of air conditioned areas are served by enthalpy controlled free cooling; |  |  |  |
| ☐ |  | At least 50% of total supply air flow rate of all PAU/ AHU are supplied by VSD fans; |  |  |  |
| ☐ |  | At least 50% of total supply air flow rate of all FCU are supplied by VSD fans; |  |  |  |
| ☐ |  | At least 50% of total chilled water flow rate of all chilled water pumps are VSD driven; |  |  |  |
| ☐ |  | At least 50% of total condensing water flow rate of all condensing water pumps are VSD driven; |  |  |  |
| ☐ |  | Having "automatic tube cleaning systems" on all water-cooled chillers; |  |  |  |
| ☐ |  | Electronic ballasts for all fluorescent lamps; |  |  |  |
| ☐ |  | Replacing >80% of T8 to T5; |  |  |  |
| ☐ |  | At least 30% of all areas are served by LED lighting; |  |  |  |
| ☐ |  | At least 30% of all public areas such as corridors, toilets, etc. are served by lighting with motion/ occupancy sensor controls; |  |  |  |
| ☐ |  | At least 30% of all areas accessible to daylight are served by lighting with dimming controls to adjust lighting level to suit the space's need; |  |  |  |
| ☐ |  | Having separate lighting controls for the window perimeter and that for the interior. Lighting at the window perimeter can be turned down or off on a sunny day; |  |  |  |
| ☐ |  | At least 50% of all window areas with direct access to daylight are applied with solar window film (i.e. windows that are heavily shaded or not having a direct view to the sky are excluded); |  |  |  |
| ☐ |  | At least 30% of all lift motor power are re-generative lift; |  |  |  |
| ☐ |  | At least 30% of all lift motor power are Variable Voltage Variable Frequency (VVVF) drives and/or direct current motor controlled by solid-state elements for lifts; |  |  |  |
| ☐ |  | At least 30% of all escalator motor power are VVVF drive systems and high gear systems for escalators; |  |  |  |
| ☐ |  | At least 30% of all escalator motor power are controlled by optical sensors to allow escalators to be stopped or slowed down when there are no users; |  |  |  |
| ☐ |  | At least 50% of all lift (by quantity) have automatic switch off lighting and ventilation fan inside the lift car when the lift is in standby/ idle mode; |  |  |  |
| ☐ |  | Adding harmonics filter to reduce total harmonics distortion (THD) in electricity distribution system; |  |  |  |
| ☐ |  | Having heat pump pre-heating at least 50% of domestic hot water (by quantity of sanitary fitting); |  |  |  |
| ☐ |  | Having thermostat on/off and/or speed control for exhaust fans serving at least 50% of plant rooms area but exclude those rooms that require continuous exhaust due to health and safety issues (e.g. chemical storage room, refuse storage room); and |  |  |  |
| ☐ |  | Openable windows for mixed mode/ natural ventilation. |  |  |  |
| Explanation to fulfill BEAM Plus criteria: |  |  |  |  |  |
| Enclosures: |  |  |  |  |  |
| ☐ | A short report on the details of the practices and measures. |  |  |  |  |
| ☐ | Other supporting documents, please specify. |  |  |  |  |