| Project Name: |  |  |  |  | CIR Applied: | Y | N |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Project Code: |  |  |  |  | CIR Number: |  |  |  |  |
| Extent of Application: |  | All Space Types |  |  |  |  |  |  |  |
| Objectives: |  | Ensure the quality of drinking water delivered to the occupants is satisfactory. |  |  |  |  |  |  |  |
| Credit Requirement: |  | For the assessment boundary with potable water supply: 1 credit point for demonstrating that the quality of drinking water meets the Water Supplies Department (WSD)'s latest guideline. Parameter(s); Criteria. Chemical and Physical. Turbidity; ≤ 3.0 NTU. Colour; ≤ 5 Hazen Unit. pH at 25°C; ≥ 6.5 and ≤ 9.5. Free Residual Chlorine; > 0 mg/L and ≤ 1.5 mg/L. Conductivity at 25°C; ≤ 500 µS/cm. Metals. Lead; ≤ 10 µg/L. Chromium; ≤ 50 µg/L. Nickel; ≤ 70 µg/L. Cadmium; ≤ 3 µg/L. Copper; ≤ 2000 µg/L. Antimony; ≤ 20 µg/L. Bacteriological. Heterotrophic Plate Count; ≤ 20 cfu/mL. E. Coli; 0 cfu/100 mL. The water quality survey should be conducted by a HOKLAS accredited laboratory and water sampling should be systematic, following the latest WSD’s water sampling protocol for commissioning of freshwater plumbing system. |
| Credit Point(s) Attainable: |  |  | 1 |  |  |  |  |  |  |
| Credit Point(s) anticipated for this submission: |  |  |  | 1 |  |  |  |  |  |
| COMPLIANCE |  |  |  |  |  |  |  |
|  | Quality of drinking water can meet WSD's latest guideline |  |  |  |  |  |  |  |  |
|  | The water quality survey conducted by a HOKLAS accredited laboratory is demonstrated |  |  |  |  |  |  |  |  |

SUBMITTALS

| Supporting Documents Please provide below softcopies with filename prefix as indicated on leftmost column. |  |  |
| --- | --- | --- |
| WU-04-03_00 | BEAM Plus Interiors submission form for WU-04-03 |  |
| WU-04-03_01 | Laboratory test report by HOKLAS laboratory(s) |  |
| WU-04-03_02 | Plumbing schematic and layout drawing(s) with all sampling points and distribution route clearly indicated |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)