## Sheet1
BEAM Plus for New Data Centres
Form SS-04-02
Stormwater Management
(BEAM Plus NDC V1.0)
Project Name: |  |  |  | Project Code:
Site Area (m2):
Design daily total rainfall intensity (H) assumed in calculation (mm/event): 30mm/event for 1 credit; 40mm/event for 1 BONUS credit
Total stormwater detention storage volume provided (m3): |  |  |  | Total stormwater detention storage volume required (m3):
Surfaces/ substrates |  | Default Runoff Coefficients Range (ᵩ) [1] | Design Runoff Coefficients (ᵩ) [2] | Areas (A) (m2) | Stormwater Detention Storage Volume required (V) (m3) [3]
Water bodies |  | 1 |  |  |  | 0
Flat roof/ road/ hardscape with impervious construction |  | 0.80-0.90 |  |  |  | 0
Flat roof covered with pebbles |  | 0.60-0.70 |  |  |  | 0
Green roof (soil depth of at least 300mm) |  | 0.30-0.40 |  |  |  | 0
Earth-covered (soil depth not more than 500mm) basement |  | 0.30-0.40 |  |  |  | 0
Pervious paving and construction [4] |  | 0.08-0.45 |  |  |  | 0
At-grade softscape |  | 0.15 |  |  |  | 0
Earth-covered (soil depth more than 500mm) basement |  | 0.15 |  |  |  | 0
(Insert row here for other surfaces/ substrates if needed) |  | - |  |  |  | 0
0
Undefined areas (runoff coefficient of 1 will be assumed for areas with no specification on surfaces/ substrates) |  | 1 | 1 |  |  | 0
Guidance Notes for Stormwater Detention Storage Volume Calculation:
1 | The default runoff coefficients range have made reference to the design guides for stormwater management/ runoff control GB50014 and DB11/685 of PRC.
2 | The design runoff coefficient to be entered. For runoff coefficients proposed not within the default runoff coefficients range, justification should be provided for approval.
3 | Stormwater Detention Storage Volume required (V)= 10 x H x ᵩ x A / 10000] (m3)
4 | Pervious paving and construction (maximum slope of porous pavement surface to a gradient of 1:20; and the minimum permeability coefficient under 15°C for permeable paving / construction should be 1.0 x 10-2 cm/s)