| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DCs |
| --- | --- |

| Objective | Reduce the consumption of non-renewable energy and the associated carbon dioxide (CO2) emissions to the atmosphere. |
| --- | --- |

| Credit Requirement | Predicted Power Usage Effectiveness (PUE) Demonstrate and quantify the proposed DC energy performance operating under Hong Kong climatic conditions at 75% of the design IT load and express them in terms of Power Usage Effectiveness (PUE). 1 to 15 credits for exact design PUE value of 1.77 to 1.52 at 75% design IT load: Additional of 2 BONUS credits for design PUE value lower than 1.5 and 1.4, respectively. Credit point(s); PUE at 75% Design IT Load. 1; 1.77. 2; 1.74. 3; 1.71. 4; 1.68. 5; 1.65. 6; 1.62. 7; 1.60. 8; 1.59. 9; 1.58. 10; 1.57. 11; 1.56. 12; 1.55. 13; 1.54. 14; 1.53. 15; 1.52. 15 + 1B; 1.50. 15 + 2B; 1.40. |
| --- | --- |

| Credit(s) Attainable | 15 + 2 BONUS |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

Please select the points to achieve:

| Targeted Achievement | Credit point to achieve |  |
| --- | --- | --- |
| Targeted PUE at 75% Design IT Load |  |  |
| 1.77 | 1 |  |
| 1.74 | 2 |  |
| 1.71 | 3 |  |
| 1.68 | 4 |  |
| 1.65 | 5 |  |
| 1.62 | 6 |  |
| 1.60 | 7 |  |
| 1.59 | 8 |  |
| 1.58 | 9 |  |
| 1.57 | 10 |  |
| 1.56 | 11 |  |
| 1.55 | 12 |  |
| 1.54 | 13 |  |
| 1.53 | 14 |  |
| 1.52 | 15 |  |
| 1.50 | 15 + 1B |  |
| 1.40 | 15 + 2B |  |

SUBMITTALS

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-01-02_00 | BEAM Plus NDC submission template for EU-01-02 |  |  |
| EU-01-02_01 | Endorsed Building Energy Simulation Report |  |  |
| EU-01-02_02 | CV of the professional as per requirements in the assessment |  |  |
| EU-01-02_03 | Input and Output Simulation Summary |  |  |
| EU-01-02_04 | Supporting documents for input, based on project development status, including: - OTTV calculation sheet based on the requirements of Buildings Department for proposed case; - Indoor design criteria from project team highlighting indoor thermal condition, occupancy density, fresh air flow rate requirement, internal load, equipment load and ventilation rate; - System and equipment specifications (for PA) and schedules (and catalogues) (PA and FA): - All air-conditioning equipment highlighting COP, cooling/ heating capacity, input power, flow rate, etc., as well as energy recovery appliance highlighting efficiency; - All lift and escalator highlighting capacity, motor power and energy saving control system - All water heater (if applicable) highlighting installed power; - All ventilation fans highlighting input power and flow rate; - All lighting fixtures highlighting designed space-specified LPD and/or input lighting power; - Design IT Equipment Loads; and - Other system (e.g. on-site renewable energy system) highlighting the key energy performance parameters - Pre-input calculation for modelling (if any), including but not limited to: - Simplified Fan Power input; and - Lighting Power Density. - Exceptional calculation; - Schematics drawings for building services systems; and - Layout plan for building services systems (optional for PA). |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)