| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC |
| --- | --- |

| Objective | Encourage the use of high efficiency cooling system in equipment and system configuration to minimise the energy consumption. |
| --- | --- |

| Credit Requirement | (a) Air-cooled Cooling System 1 to 2 credits for demonstrating the total cooling system efficiency serving data hall is of 0.85 kW/ton and 0.78 kW/ton, respectively. OR (b) Water-cooled Cooling System 1 to 2 credits for demonstrating the total cooling system efficiency serving data hall is of 0.8 kW/ton and 0.75 kW/ton, respectively. Note: For DC equipped with combined system type, the assessment will be based on the dominated plant, i.e., at least 75% of actual cooling consumption by the dominated system. |
| --- | --- |

| Credit(s) Attainable | 2 |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

Cooling System adopted at the Project DC:

| Air-cooled Cooling System |  | Air-cooled Cooling System |  |
| --- | --- | --- | --- |

Please confirm that the following requirement is met by checking the box with .

| Air-cooled Cooling System |  |  |
| --- | --- | --- |
| The prescribed system efficiency shall be achieved at 75% of the design IT load |  |  |
| The system efficiency calculation should include the following components: |  |  |
| Air Cooled Chilled-Water Plant: - Air-cooled Chiller - Chilled Water Pump Unitary Air-Conditioners: - Variable Refrigerant Flow (VRF) System - Single-Split Unit - Multi-Split Unit |  |  |
| Total Cooling System Efficiency |  |  |
| Water-cooled Cooling System |  |  |
| The prescribed system efficiency shall be achieved at 75% of the design IT load |  |  |
| The system efficiency calculation should include the following components: |  |  |
| Water Cooled Chilled-Water Plant: - Water-cooled chiller - Chilled water pump - Condenser water pump - Cooling tower or Heat rejection unit |  |  |
| Total Cooling System Efficiency |  |  |

SUBMITTALS

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-03-04_00 | BEAM Plus NDC submission template for EU-03-04 |  |  |
| EU-03-04_01 | Endorsed technical report |  |  |
| EU-03-04_02 | Design report showing the design IT load |  |  |
| EU-03-04_03 | Cooling system equipment schedule showing all technical information of the system components |  |  |
|  | Catalogue of all the system components |  |  |
| EU-03-04_04 | Water-side schematic and layout drawings highlighting all the system components |  |  |
| EU-03-04_05 | Test and commissioning records |  |  |
| EU-03-04_06 | CV of the professional as per requirements in the assessment |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)