| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC |
| --- | --- |

| Objective | Encourage the use of high efficiency air distribution system to minimise the energy consumption |
| --- | --- |

| Credit Requirement | 1 to 2 credit points for demonstrating the total air flow efficiency of the air distribution system serving all data hall, from supply to return, is of 0.9 kW/m³/s and 0.8 kW/m³/s, respectively. |
| --- | --- |

| Credit(s) Attainable | 2 |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

Please confirm that the following requirement is met by checking the box with .

| The prescribed system efficiency shall be achieved at 75% of the design IT load |  |
| --- | --- |
| The calculation of air flow efficiency included both the supply and return air flows serving each data hall |  |

SUBMITTALS

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-03-05_00 | BEAM Plus New DCs submission template for EU-03-05 |  |  |
| EU-03-05_01 | Endorsed technical report |  |  |
| EU-03-05_02 | Data hall layout plan |  |  |
| EU-03-05_03 | Data hall air-distribution system equipment schedule showing the information of fan power and flow rate |  |  |
|  | Catalogue of all the supply and return fans |  |  |
| EU-03-05_04 | Data hall Air-side schematic and layout drawings highlighting all the supply and return fans. |  |  |
| EU-03-05_05 | Test and Commissioning records |  |  |
| EU-03-05_06 | CV of the professional as per requirements in the assessment |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)