| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC |
| --- | --- |

| Objective | Ensure the DC building are in comfortable acoustic environment. |
| --- | --- |

| Credit Requirement | (a) Data Hall Noise Control 1 credit point for demonstrating the internal noise level at data hall area are maintained at an appropriate level. (b) Noise Isolation 1 credit point for demonstrating airborne noise isolation between rooms, spaces and premises fulfils the prescribed criteria. (c) Background Noise 1 credit point for demonstrating background noise levels within the prescribed criteria (including traffic noise and external building service equipment that are within the project boundary). |
| --- | --- |

| Credit(s) Attainable | 3 |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

- Data Hall Noise Control

1) Please fill in the blanks and confirm that the following requirement is met by checking the box with .

| Data hall | Space (m2) | Sampling point locations | Methodology adopted |  | Internal noise level, dB (A) | Compliance, i.e. 5 dB(A) better than First Action Level a daily personal noise exposure (LEP, d) of 85 dB(A). |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculations | Measurements |  |  |

- Noise Isolation

1) Please fill in the blanks and confirm that the following requirement is met by checking the box with .

| Type of Premises | Locations | Total Area of relevant space type (m2) | Methodology adopted |  | Compliance |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculations | Measurements | Weighted SRI |  | Level Difference |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |

- Background Noise

Please fill in the blanks and confirm that the following requirement is met by checking the box with .

| Type of Premises | Locations | Total Area of relevant space type (m2) | Methodology adopted |  | Compliance (NC or NR to be used consistently in the project) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculations | Measurements | NC |  | NR |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |
| Office Type Premises |  |  |  |  | 40 |  | 40 |  |

SUBMITTALS

- Data Hall Noise Control

| Supporting Documents. |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-03a_00 | BEAM Plus NDC submission template for HWB-03-03 |  |  |
| HWB-03-03a_01 | Schedule of spaces cross-referencing to the GBP showing the data hall present in the building. |  |  |
| HWB-03-03a_02 | Data hall noise calculation report at representative locations with supporting documents including noise data of the installed IT equipment and Building Service Equipment in data hall |  |  |
| HWB-03-03a_03 | Data hall noise measurement report at representative locations with supporting documents including noise data of the installed IT equipment and Building Service Equipment in data hall |  |  |
| HWB-03-03a_04 | CV of the professional as per requirements in the assessment |  |  |

- Noise Isolation

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-03b_00 | BEAM Plus NDC submission template for HWB-03-03 |  |  |
| HWB-03-03b_01 | Schedule of spaces cross-referencing to the GBP showing the types of premises present in the building. |  |  |
| HWB-03-03b_02 | Airborne noise isolation computer simulation/ calculation report (Applicable to computer simulation/ calculation route only) |  |  |
| HWB-03-03b_03 | Endorsed report on airborne noise isolation measurement at representative locations (Applicable to measurement route only) |  |  |
| HWB-03-03b_04 | CV of the professional as per requirements in the assessment |  |  |

- Background Noise

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-03c_00 | BEAM Plus NDC submission template for HWB-03-03 |  |  |
| HWB-03-03c_01 | Schedule of spaces cross-referencing to the GBP showing the types of premises present in the building |  |  |
| HWB-03-03c_02 | Background noise computer simulation/ calculation report |  |  |
| HWB-03-03c_03 | Endorsed background noise measurement report |  |  |
| HWB-03-03c_04 | CV of the professional as per requirements in the assessment |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)