| Credit Requirement: |  |  | 1 credit for complying with the recommendations given in the Code of Practice - Prevention of Legionnaires Disease, in respect of air-conditioning and ventilation systems and water systems. |  |  |
| --- | --- | --- | --- | --- | --- |
| Credit Attainable: |  |  |  | 1 |  |
| Credit anticipated for this submission: |  |  |  |  |  |
| Checklist: |  |  |  |  |  |
| ☐ |  | Cooling Towers: - Implement an effective water treatment program; - Continuous bleed-off of cooling water; and - Routine Cleaning and Disinfection. |  |  |  |
| ☐ |  | Components in Air-conditioning Systems except Cooling Towers: - Drain trays and horizontal drain pipes are regularly inspected and cleaned; - Air filters in air conditioning system are regularly cleaned or replaced; and - Steam or ultrasonic humidifiers are used, Alternatively, When recirculating water spray humidifiers are used, the water reservoirs are drained each day and the system are disinfected at least once every six months or after shut down for over a month. |  |  |  |
| ☐ |  | Plumbing and Drainage System: - Fresh water storage tanks are drained and cleaned on a quarterly basis; - Cold water outlets which are infrequently used or are connected to stagnant water supply pipework are flushed at full flow for a minimum period of one minute at least on a weekly basis and before use; and - Purge valves are provided at the pipe ends of all unavoidable spurs or stagnant points in the pipework for draining/purging the dead ends for a minimum period of one minute at least on a weekly basis. |  |  |  |
| ☐ |  | Centralized hot water supply systems: - Hot water storage devices shall be operated at 60ºC or above; - Hot water storage devices are cleaned at least once per year; and - Hot water outlets which are infrequently used or are connected to stagnant water supply pipework are flushed at full flow for a minimum period of one minute at least on a weekly basis and before use. |  |  |  |
| ☐ |  | Fountains: - The installation, including filters and strainers, are regularly cleaned or replaced; - A small volume of pool water are drained regularly and replenished with fresh water; and - Implement an effective water treatment program. |  |  |  |
| ☐ |  | Spa Pools: - The spa pool water are continuously recirculated, filtered and disinfected, and with pH control to maintain a pH value of 7.2 to 7.8; - The spa pool system are checked daily before opening, periodically throughout the day and after closing the spa pool, and be drained and cleaned at least once a week; and - Monthly, quarterly and annual programmes for checking and cleaning all equipment of the spa pool are implemented. |  |  |  |
| Explanation to fulfill BEAM Plus criteria: |  |  |  |  |  |
| Enclosures: |  |  |  |  |  |
| ☐ | The design and justification on fulfilling the credit requirement. |  |  |  |  |
| ☐ | Other supporting documents, please specify. |  |  |  |  |