## Detail (EBv2.0)
BEAM Plus Existing Buildings (Version 2.0) Credit Summary Comprehensive Scheme
BEAM Plus Project No:
Project Name:
Comprehensive Scheme A / B :
Provisional Assessment (PA) / Final Assessment (FA):
1. | Project Description:
2 | Submission Schedule: (applicable to Comprehensive Scheme B only)
|  | 1st Submission: | MAN / SA / MWA/ EU/ WU/ IEQ/ IA *
|  | 2nd Submission: | MAN / SA / MWA/ EU/ WU/ IEQ/ IA *
|  | ____ Submission: | MAN / SA / MWA/ EU/ WU/ IEQ/ IA *
Final Submission
* Please delete as appropriate

## Summary
2. Credit Summary
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Management (MAN) |  |  |  | 23+6B | Y/N?
MAN P1 | Green Purchasing Plan | Demonstrate that green purchasing plan and procedures (including both materials and services) either follow their internal company guideline or other international standards, shall be in place. | None. | Required | Y | Required
MAN 1 | EHS and Energy Management System | 1 credit where the building management operates an Environmental Management System (EMS) certified to ISO 14001. | None. | 1 | Y
|  | 1 credit where the building management operates an Occupational Health and Safety System (OHSAS). |  | 1 | Y
|  | 1 credit where the building management operates an Energy Management System (EnMS). |  | 1 | Y
|  | 1 Bonus credit where building management operates an OHSAS certified to BS OHSAS 18001. |  | 1B | Y |  | B
|  | 1 Bonus credit where the building management operates an EnMS certified to ISO 50001. |  | 1B | Y |  | B
MAN 2 | Environmental, Social and Governance (ESG) Disclosure | 1 credit where the Building Owner/ Building Management Company discloses sustainability policy and targets to the public. | None. | 1 | Y
|  | 1 Bonus credit where the Building Owner/ Building Management Company follows Global Reporting InitiativeTM (GRI) Sustainability Reporting Guidelines and discloses the G4 sustainability report to the public. |  | 1B | Y |  | B
MAN 3 | BEAM Professional | 1 credit for at least 2 members from the Building Management Company are certified BEAM Professional with EB credential. Alternatively 1 credit for at least 1 key member from the Building Management Company is a certified BEAM Professional with EB credential and at least 1 member is a certified BEAM Affiliate. | None. | 1 | Y
|  | 1 additional credit for the building-in-charge being a certified BEAM Professional with EB credential and with at least 1 professional corporate membership qualification (e.g. HKIH, HKIA, HKIE, HKIS (BS/PFM), RICS (BS/FM), IFMA, HKIFM, BSOMES, or equivalent). |  | 1 | Y
MAN 4 | Staff Training and Resources | a) Staff and Technical Resources 1 credit for having adequate staff and technical resources to meet the O&M requirements of the building. | None. | 1 | Y
|  | b) Staff Training 1 credit for providing adequate and periodic training for the staff responsible for the O&M of the building. |  | 1 | Y
MAN 5 | Building and Site Operation and Maintenance | a) Building Maintenance 1 credit for demonstrating the operation of a planned programme of regular inspection, cleaning and maintenance of the building’s fabric and structure under the control of the Applicant. | None. | 1 | Y
|  | b) External Areas and Facilities 1 credit for demonstrating the operation of a planned programme of regular inspection, cleaning and maintenance of external areas and facilities. | Building footprint exceeds 80% of the site area. | 1 | Y
MAN 6 | Building Services Operation and Maintenance | a) Central Heating Ventilation and Air-Conditioning (HVAC) Plant 2 credits for demonstrating the operation of a planned programme of regular inspection and maintenance of the central HVAC plant. | Building does not have a central HVAC plant | 2 | Y
|  | b) Other Engineering Systems Maximum 4 credits for demonstrating the operation of a planned programme of regular inspection and maintenance of the following listed systems: i. Air-conditioning system except central HVAC plant; ii. Electrical system; iii. Lighting system; and iv. Plumbing and Drainage system. | None. | 4 | Y
|  | c) Assessment of Operation & Maintenance Practice 1 credit for having undertaken an audit of the effectiveness of the O&M practices for all building services engineering systems. | None. | 1 | Y
MAN 7 | Electronic Operation and Maintenance Platform | 1 Bonus credit for operating an electronic O&M platform by the Building Owner/ Building Management Company. | None. | 1B | Y |  | B
MAN 8 | IAQ Management for Renovation | 1 credit for providing a Construction Indoor Air Quality (IAQ) Management Plan. | None. | 1 | Y
|  | 1 credit for providing records that the Construction IAQ Management Plan has been implemented by the Building Owner/ Building Management Company/ tenants during renovation. |  | 1 | Y | 0
MAN 9 | Green Cleaning | a) Implementation of Green Cleaning 1 credit for demonstrating the appropriate green cleaning procedures/ practices for the project. | None. | 1 | Y
|  | b) Use of Green Cleaning Detergent 1 credit for demonstrating the use of at least 10% of green cleaning detergents. |  | 1 | Y
|  | 1 Bonus credit for demonstrating the use of at least 20% of green cleaning detergents. |  | 1B | Y |  | B
MAN 10 | Integrated Pest Management | 1 credit for implementing an integrated programme for pest management. | None. | 1 | Y
MAN 11 | User Guidance | 1 credit for providing user guide to encourage and promote environmentally friendly activities. | None. | 1 | Y
MAN 12 | Green Lease | 1 Bonus credit for implementing green lease to the tenants of the buildings. | Buildings without any tenants. | 1B | Y |  | B
Credit Applicable: |  |  |  |  | 23+6B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Site Aspects (SA) |  |  |  | 22+3B | Y/N?
SA 1 | Green Building Attributes | Maximum 7 credits for the building that has been certified under BEAM Plus New Buildings (Version 1.1 or 1.2)/ BEAM 4/04 or 5/04: i. 7 credits for Platinum grade; ii. 6 credits for Gold grade; and iii. 5 credits for any other grade. Alternatively Maximum 5 credits for an uncertified building that meets the listed performance characteristics. | None. | 7 | Y
SA 2 | Noise Pollution | a) Provision of Acoustic Treatment 1 credit for providing adequate acoustic treatment to the following building services equipment: chillers, cooling towers, ventilation fans with Sound Power Level (SWL) higher than 80 dB(A). | None. | 1 | Y
|  | b) Demonstration of Compliance with HKPSG Criteria 1 credit for demonstrating that the level of the intruding noise at the façade of the potential Noise Sensitive Receivers (NSRs) is in compliance with the criteria recommended in the Hong Kong Planning Standards and Guidelines (HKPSG). |  | 1 | Y
SA 3 | Light Pollution | 2 credits if there are no external lightings installed for the building. Alternatively 1 credit for switching off the Building Owner/ Building Management Company’s external lightings from 23:00 to 07:00. 1 additional credit for liaising with tenants and requiring them to switch off the external lightings from 23:00 to 07:00. | None. | 2 | Y
SA 4 | Heat Island Reduction | 1 credit for demonstrating the implementation of any combination of the following strategies for a minimum of 10% of the external non-roof area (i.e. ground floor and podium with less than 15m in height): i. Greenery; ii. Water feature; iii. Green wall or vertical greening; iv. Shading device; and/or v. Paving materials with solar reflectance (SR) of 0.33. | None. | 1 | Y
|  | 1 to 2 Bonus credit(s) for more than 20% or 30% of the external non-roof area covered with the aforesaid features. |  | 2B | Y |  | B
SA 5 | Green Roof | 1 Bonus credit for providing green roof and/or organic farm for at least 20% of the available main roof area. | None. | 1B | Y |  | B
SA 6 | Corporate Social Responsibility Facilities/ Services | Maximum 4 credits for providing the following listed CSR facilities/ services: i. Allowing persons with visual impairment to bring along with their guide dogs; ii. Automated External Defibrillator; iii. Baby-care room; iv. Bicycle parking; v. Breast feeding room; vi. Free baby stroller lending service; vii. Free drinking fountain; viii. Free wheelchair lending service; ix. Free Wi-Fi in common area; x. Organic farm; xi. Permanent art work; xii. Permanent green building education show board; and xiii. Others to be proposed by the Applicant. | None. | 4 | Y
SA 7 | Amenities for Operation and Maintenance | Maximum 3 credits for providing the following listed amenities that improve the operation and maintenance of the building and its engineering services: i. Aerial working platform; ii. Building Management System (BMS); iii. Cat ladder; iv. Davit arm system; v. External pipe duct; vi. Fall arrest system; vii. Gondola system; viii. Guard room; ix. Maintenance platform; x. Maintenance workshop; xi. Movable platform, and xii. Others to be proposed by the Applicant. | None. | 3 | Y | 0
SA 8 | Barrier Free Access | Maximum 3 credits for providing enhanced barrier free access provisions as per the latest version of the Design Manual of Barrier Free Access. | None. | 3 | Y
Credit Applicable: |  |  |  |  | 22+3B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Materials and Waste Aspects (MWA) |  |  |  | 17+7B | Y/N?
MWA P1 | Waste Recycling Facilities | Providing spaces for the collection, sorting, storage and disposal of waste and recovered materials. | None. | Required | Y
MWA P2 | Materials Purchasing Plan | Demonstrating that the plan of material procurement (sub-section under MAN P1 Green Purchasing Plan) and its procedures for both on-going consumables and durable goods either following the internal company guideline or other international standards are in place. | None. | Required | Y
MWA 1 | Materials Purchasing Practices | 1 to 2 credit(s) for demonstrating at least 50% or 70% of purchased on-going consumables are environmentally friendly products for the past 12 months as minimum. | None. | 2 | Y
|  | 1 to 2 credit(s) for demonstrating at least 50% or 70% of purchased durable goods are environmentally friendly products for the past 12 months as minimum. |  | 2 | Y
|  | 1 credit for demonstrating at least 70% of purchased both on-going consumables and durable goods are environmentally friendly products for the past 24 months. |  | 1 | Y
|  | 1 Bonus credit for demonstrating at least 70% of purchased both on-going consumables and durable goods are environmentally friendly products for the past 36 months. |  | 1B | Y |  | B
MWA 2 | Use of Certified Green Products | Maximum 2 Bonus credits for purchasing green products certified by Construction Industry Council (CIC) Carbon Labelling Scheme/ HKGBC Green Product Accreditation and Standards (HK G-PASS) or other internationally recognised schemes. | None. | 2B | Y |  | B
MWA 3 | Ozone Depleting Substances | a) Newly and Existing Installed Equipment using Refrigerants 1 credit for all the equipment (both newly purchased and existing) using the refrigerants with Global Warming Potential (GWP) less than 1,900. Alternatively, for equipment with refrigerant GWP value > 1,900, credit can be achieved when the Applicant can demonstrate a phased programme of refrigerant replacement. | None. | 1 | Y
|  | 1 credit for using refrigerants with a combined value less than or equal to the threshold for the combined contributions to ozone depletion and global warming potentials for all new and existing HVAC&R equipment that under the control of Applicant. |  | 1 | Y
|  | b) Fire Suppression Materials 1 credit for using the fire suppression and other materials that avoids the use of ozone depleting substances in their manufacture, composition or use. |  | 1 | Y
MWA 4 | Waste Management Plan | 1 credit for developing a waste management plan. | None. | 1 | Y
MWA 5 | Recycling Facilities for Different Waste Streams | Maximum 4 credits for providing the following listed on-site recycling facilities and implementing the materials collection arrangement: i. Fluorescent lamp (CFLs and fluorescent tubes); ii. Glass bottle; iii. Rechargeable battery; and iv. Waste Electrical and Electronic Equipment (WEEE). | None. | 4 | Y
MWA 6 | Food Waste Management | 1 credit for signing the Food Wise Charter and demonstrating the implementation of food waste reduction good practice guide as per Hong Kong Food Wise Campaign. | None. | 1 | Y
|  | 1 Bonus credit for providing on-site used cooking oil collection facility and implementing the collection arrangement. |  | 1B | Y |  | B
MWA 7 | Waste Treatment Equipment | 1 Bonus credit for providing at least one set of waste treatment equipment. | None. | 1B | Y |  | B
MWA 8 | Action to Waste Reduction | a) Implementation of the Waste Management Plan 1 credit for demonstrating the implementation of the waste management plan. | None. | 1 | Y
|  | b) Waste Stream Audit 1 Bonus credit for undertaking a waste stream audit. |  | 1B | Y |  | B
|  | c) Waste and Recycling Records 1 credit for the collection of the waste and recycling records for past 12 months. |  | 1 | Y
|  | 1 Bonus credit for the collection of the waste and recycling records for the past 24 months. |  | 1B | Y |  | B
|  | d) New Targets on Waste Recycle/ Reduction 1 credit for providing new targets on the waste recycle items, recycle rate and reduction rate based on the performance of the past 12 months. |  | 1 | Y
Credit Applicable: |  |  |  |  | 17+7B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Energy Use (EU) |  |  |  | 39+9B | Y/N?
EU P1 | Minimum Energy Performance | Conduct energy audit in accordance with the Buildings Energy Efficiency Ordinance (Cap. 610) requirements for existing buildings. | Buildings not covered by BEEO. | Required | Y
EU 1 | Energy Management | a) Energy Management Policy 1 credit for an energy management policy endorsed by top management. | None. | 1 | Y
|  | b) Energy Management Plan 1 credit for energy management plan covering less than 3 years. 2 credits for energy management plan covering 3 years or more. | None. | 2 | Y
|  | c) Appointment of Energy Warden 1 credit for appointing an Energy Warden in the Building Management Company. | None. | 1 | Y
EU 2 | Energy Analysis | a) Data Collection Facilities 1 credit for sub-metering systems for any 3 of the following electrical loads where applicable: i. Chiller plant; ii. Cooling tower plant; iii. Lift; iv. Escalator; v. Lighting; and vi. Plumbing & drainage. | Building to compulsorily comply with BEC 2012 or later version | 1 | Y
|  | 1 credit for having Building Management System (BMS) to log operation data (e.g. pressure, temperature, flow rate, on/ off status) for monitoring operation and function of the system including the following as a minimum: i. Air side; ii. Water side; iii. Cooling load; and iv. Lighting control. | Residential buildings | 1 | Y
|  | b) Data Collection Record 1 credit for providing energy consumption data record of at least 1 year for major electrical loads. 2 credits for providing energy consumption data record of 3 years or more for major electrical loads. | None. | 2 | Y
|  | c) Data Analysis 1 credit for calculating the Energy Use Intensity (EUI) of the following services in data analysis: i. Air-conditioning system; ii. Lift & escalator (if any); iii. Lighting; and iv. Others. | None. | 1 | Y
|  | d) Energy Audit Report 3 credits for filling up Table (II) to Table (VIII) under the Template 1 on Additional Information to Executive Summary of Energy Audit Report. 2 credits for completing the entire Template 1 on Additional Information to Executive Summary of Energy Audit Report to EMSD. | None. | 5 | Y
|  | e) Carbon Audit Report 1 credit for conducting carbon audit in accordance with the requirements as stipulated in the guideline issued by the Authority. | None. | 1 | Y
EU 3 | Commissioning | a) Action Plan 1 credit for action plan covering less than 3 years. 2 credits for action plan covering 3 years or more. | None. | 2 | Y
|  | b) Commissioning 1 credit for providing original/ retro-commissioning (RetroCx) for electrical services systems. 1 credit for providing original/ retro-commissioning (RetroCx) for plumbing and drainage system. 1 credit for providing original/ retro-commissioning (RetroCx) for lift and escalator system (if any). For buildings with chiller system: 1 credit for providing original/ retro-commissioning (RetroCx) for water side equipment of central air-conditioning system. 1 credit for providing original/ retro-commissioning (RetroCx) for air side equipment of central air-conditioning system. For buildings without chiller system: 1 credit for providing original/ retro-commissioning (RetroCx) for air-conditioning system. | None. | 5 | Y
|  | c) On-going Commissioning 1 credit for providing an ongoing commissioning plan detailing the works and person-in-charge for electrical services if on-going commissioning have been conducted for electrical system and/or for Heating, Ventilating, and Air-Conditioning (HVAC) system if on-going commissioning have been conducted for HVAC system. 1 credit for the execution of any 2 of the following measures for power quality management regularly. 2 credits for the execution of any 4 of the following measures for power quality management regularly. i. Power factor monitoring & correction; ii. 3-phase load balancing; iii. Maximum demand monitoring; iv. Demand Side Management (DSM); v. Total Harmonic Distortion (THD); and vi. Thermal scan on electrical distribution system. For buildings with chiller system: 1 credit for ongoing commissioning for water side equipment of central air-conditioning system. 1 credit for ongoing commissioning for air side equipment of central air-conditioning system. For buildings without chiller system: 1 credit for ongoing commissioning for all HVAC equipment. | None. | 5 | Y
EU 4 | Energy Benchmarking and Improvement | a) Benchmarking For applicable types of Buildings: Credit(s) can be achieved based on the label obtained from HKGBC Benchmarking & Energy Saving Tool – Office Buildings (HK BESTOF).. Percentile: 50th (1), 40th (3), 30th (5), 20th (1 Bonus), 10th (2 Bonus) Alternative for Commercial Buildings: Credit(s) can be achieved based on the label obtained from HKGBC Benchmarking & Energy Saving Tool – Office Buildings (HK BESTOF) by comparing with current building energy consumption. HK BESTOF: Green(1), Bronze(3), Silver(5), Gold(1 Bonus), Platinum(2 Bonus) | Building types not covered by EMSD Benchmarking Tool. | 5 | Y
|  |  |  | 2B | Y |  | B
|  | b) Self-Improvement Credit(s) can be achieved based on the reduction percentage by comparing electricity bill, Towngas bill or metering data in the category determined in part a) Benchmarking. (Baseline year can be any year in the past 5 years). i. For buildings ranked at the 40th percentile or below under EMSD Benchmarking Tool/ ”Bronze” or below label obtained from HK BESTOF: Annual energy use reduction: 2%(1), 4%(2), 6%(3), 8%(4) ii. For buildings ranked at the 20th or 30th percentile under EMSD Benchmarking Tool/ ”Gold” or “Silver” label obtained from HK BESTOF: Annual energy use reduction: 1%(1), 2%(2), 3%(3), 4%(4) iii. For buildings ranked at the 10th percentile under EMSD Benchmarking Tool or “Platinum” label obtained from HK BESTOF: Annual energy use reduction: 0.5%(1), 1%(2), 1.5%(3), 2%(4) iv. For buildings which are excluded in part (a) Benchmarking: Annual energy use reduction: 1%(1), 2%(2), 3%(3), 4%(4), 6%(1 Bonus), 8%(2 Bonus) | None. | 4 | Y
|  |  |  | 2B | Y |  | B
|  | c) Peak Electricity Demand Reduction Credit(s) can be achieved based on the reduction percentage in the peak electricity demand. Commercial and Hotel Buildings: 10%(1), 15%(2), 20%(3) Educational Buildings (Centralised Air Conditioning System): 10%(1), 15%(2), 20%(3) Educational Buildings (Unitary Air-conditioner): 5%(1), 10%(2), 15%(3) Other Building Types: 5%(1), 10%(2), 15%(3) | Residential Buildings or Buildings not charged by either Bulk Tariff, Large Power Tariff or Maximum Demand Tariff*. | 3 | Y
EU 5 | Enhancement | Maximum of 1 Bonus credit for each energy conservation approach is allowed but the award of credit is subject to final approval of BEAM Society Limited (BSL)’s Technical Review Committee (TRC) based on the estimated energy reduction, justification and/or the innovation of the proposed approaches. a) Research and Development in Energy 1 Bonus credit for conducting research and development or participating in competition with published paper related to energy aspects. b) Compliance with the BEC Maximum 4 Bonus credits for compliance with the latest version of the following listed BEC (This bonus credit does not apply to those buildings that are required to comply with the latest version of the BEC): i. Energy Efficiency Requirements of Air-Conditioning Installations; ii. Energy Efficiency Requirements of Electrical Installations; iii. Energy Efficiency Requirements of Lighting Installations; and/or iv. Energy Efficiency Requirements of Lift and Escalator Installations. c) Renewable Energy System 1 Bonus credit where at least 0.2% of building energy consumption in communal area is obtained from renewable energy sources. d) Separate Energy Charges 1 Bonus credit where separate charges are made for energy use. e) Other Approaches Maximum 7 Bonus credits for adopting other energy conservation approach not prescribed above. | None. | 7B | Y | 0 | B
Credit Applicable: |  |  |  |  | 39+9B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Water Use (WU) |  |  |  | 23+8B | Y/N?
WU P1 | Water Conservation Plan | Developing a water conservation plan endorsed by top management. | None. | Required | Y
WU P2 | Water Efficient Devices | At least 80% of all water taps and shower heads for bathing (if any) installed are with Water Efficiency Labelling Scheme (WELS) Grade 2 or above. Alternatively Demonstrating that the use of water efficient devices leads to an estimated aggregate annual saving of 5%. | Water devices installed at tenants’ areas can be excluded from the assessment. | Required | Y
WU P3 | Water Quality Survey | Requirement Demonstrating that the quality of fresh water at all fresh water tanks and the farthest supply point of each water tank meets WSD’s requirements. | None. | Required | Y
WU 1 | Water Efficient Devices | Credit(s) can be achieved based on the estimated aggregate annual saving by the use of water efficient devices. Estimated aggregate annual fresh water saving: 10%(1), 15%(2), 20%(3), 25%(4) | Water devices installed at tenants’ areas can be excluded from the assessment. | 4 | Y
WU 2 | Water Use For Irrigation | 1 credit for limited use of fresh water for irrigation. Alternatively 1 credit for demonstrating the use of highly efficient irrigation technologies and/or harvested rainwater or/and recycled grey water to reduce irrigation water by 25% or more in comparison with conventional irrigation method. | Project with soft landscape area less than 200m2. | 1 | Y
|  | 1 Bonus credit for reducing irrigation water by 50% or more. |  | 1B | Y |  | B
WU 3 | Cooling Tower Water | 1 credit for reducing fresh water consumption by installing water treatment system which can achieve 6 cycles of concentration with acceptable water quality. | Buildings without cooling tower or cooling tower with salt water. | 1 | Y
|  | 1 Bonus credit for achieving 7 or more cycles of concentration with acceptable water quality. |  | 1B | Y |  | B
WU 4 | Water Recycling | 1 Bonus credit for harvesting rainwater and/or recycling grey water that leads to a reduction of at least 2.5% in the consumption of fresh water. | None. | 1B | Y |  | B
|  | 1 additional Bonus credit if the reduction can achieve 5% or above. |  | 1B | Y |  | B
WU 5 | Water Saving Performance | Credit(s) can be achieved based on the reduction percentage by comparing water bill/ metering data. (Reference year can be any year in the past 5 years). Annual fresh water use reduction: 3%(1), 6%(2), 9%(3), 12%(4), 15%(Bonus) | None. | 4 | Y
|  |  |  | 1B | Y |  | B
WU 6 | Quality Water Supply Scheme for Buildings - Fresh Water | 1 to 3 credits for buildings which have been certified with Quality Water Supply Scheme for Buildings – Fresh Water (Plus). Type of Certificate: Blue(1), Silver(2), Gold(3) | None. | 3 | Y
WU 7 | Water Metering | 1 credit for permanently installation of water meters for at least 2 of the following water sub-systems: i. Irrigation; ii. Indoor plumbing fixtures and fittings; iii. Cooling towers; iv. Water features/ pools; and v. Other process water. | None. | 1 | Y
|  | 1 Bonus credit for installation of devices for detecting water leakage at the communal water supply system within the building lot, i.e. underground buried pipes and all fresh water pump rooms. |  | 1B | Y |  | B
WU 8 | Water Audit | 2 credits for undertaking a water audit and maintaining a water use inventory. | None. | 2 | Y
WU 9 | Enhancement | a) Implementation of water saving recommendations 1 credit for implementing the water saving recommendations as stipulated in the water audit. | None. | 1 | Y
|  | b) Educational/ promotional campaign 1 credit for the Building Owner/ Building Management Company to encourage building users to establish a good habit of water conservation by organising promotion campaign. |  | 1 | Y
WU 10 | Twin-tank System | Maximum 2 Bonus credits for providing twin-tank system for: i. Fresh water supply system; and ii. Flushing water supply system. | None. | 2B | Y |  | B
WU 11 | Water Efficient Flushing System | 1 credit for installing dual flush for the water closets under the control of the Applicant. | Flushing system installed at tenants’ areas can be excluded from the assessment. | 1 | Y
|  | 1 credit for installing urinal with WELS Grade 2 or above. |  | 1 | Y | 0
WU 12 | Quality Water Supply Scheme for Buildings – Flushing Water | 1 to 3 credits for buildings which have been certified with Quality Water Supply Scheme for Buildings – Flushing Water. Type of Certificate: Blue(1), Silver(2), Gold(3) | None. | 3 | Y
Credit Applicable: |  |  |  |  | 23+8B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Indoor Environmental Quality (IEQ) |  |  |  | 26+5B | Y/N?
IEQ P1 | Minimum Ventilation Performance | Demonstrate that the project is in compliance with the minimum requirements of ANSI/ASHRAE 62.1-2013 [ ] in respect of Outdoor Air Quality and Minimum Ventilation Rate. Alternatively In case of the minimum ventilation rate of ANSI/ASHRAE 62.1-2013 is not complied due to the physical constraints of the existing ventilation system, demonstrate that the system is operated at maximum outdoor air delivery rate and provide not less than 5 l/s per person of combined outdoor air rate. | Naturally ventilated spaces. | Required | Y
IEQ 1 | Building User Satisfaction Survey on Indoor Comfort | 1 credit for conducting regular building user satisfaction surveys to collect anonymous responses regarding the indoor environmental quality (e.g. hygiene, IAQ, ventilation, thermal comfort, lighting quality, aural environment etc.). | None. | 1 | Y
|  | 1 credit for implementing the recommendations for improvement of IEQ as stipulated in the survey report. |  | 1 | Y
IEQ 2 | Ventilation in Common Areas | 1 credit for providing adequate ventilation for 90% of mechanically ventilated common areas in a building. Alternatively For naturally ventilated premises, 1 credit for demonstrating that 80% of the common areas in a building are provided by natural ventilation. | None. | 1 | Y
IEQ 3 | Localised Ventilation | 1 credit for providing adequate ventilation system for rooms/ areas with significant indoor pollution sources. | None. | 1 | Y
IEQ 4 | Thermal Comfort in Air-Conditioned Premises | 1 credit for sustaining the air temperature at the design value within ±1.5°C when the air side system is operating at steady state under normally occupied periods. | Premises without any A/C provisions. | 1 | Y
|  | 1 credit for demonstrating an appropriate temperature (i.e. <25.5°C), relative humidity (i.e. <70%) and air velocity (i.e. <0.3 m/s) in the building. |  | 1 | Y
IEQ 5 | Biological Contamination | 1 credit for complying with the recommendations given in the Code of Practice - Prevention of Legionnaires Disease, in respect of air-conditioning and ventilation systems and water systems. | None | 1 | Y
IEQ 6 | Waste Disposal Facilities | 1 credit for providing de-odourising system in all rooms designated for refuse storage or materials recovery. | None. | 1 | Y
IEQ 7 | Control of Environmental Tobacco Smoke | 1 credit for implementing no smoking policy outside the building except in designated smoking areas. | None. | 1 | Y
IEQ 8 | IAQ Monitoring | Maximum 7 credits for demonstrating compliance with appropriate criteria for indoor pollutant levels, for following parameters: i. Carbon Dioxide; ii. Carbon Monoxide, Nitrogen Dioxide and Ozone; iii. Respirable Suspended Particulate; iv. Formaldehyde; v. Total Volatile Organic Compounds; vi. Radon; and vii. Bacteria. | None. | 7 | Y
|  | 1 Bonus credit where the whole building (i.e. including the tenant areas) is certified by the Good Class of ‘Indoor Air Quality Certification Scheme for Office and Public Place’. |  | 1B | Y |  | B
|  | 1 Bonus credit for demonstrating the continuous participation in the ‘Indoor Air Quality Certification Scheme for Office and Public Place’ for past 3 consecutive years. |  | 1B | Y |  | B
IEQ 9 | IAQ in Car Parks | 1 credit for complying with the recommended CO and NO2 level as stipulated in ProPECC PN 2/96. | Buildings without car park or carpark area less than 10% of construction floor area. | 1 | Y
IEQ 10 | Interior Lighting in Normally Occupied Areas | Maximum 3 credits for achieving the prescribed lighting performance in each type of premises, regarding the illuminance and lighting quality as Listed below: i. Maintained illuminance and illuminance uniformity; ii. Achieving the limiting unified glare rating; and iii. Light sources with an appropriate colour rendering index. | Residential units, hotels and apartment buildings. | 3 | Y
|  | 1 Bonus credit for fulfilling the above requirement in tenant’s areas with at least 50% coverage. | None. | 1B | Y |  | B
IEQ 11 | Interior Lighting in Areas Not Normally Occupied | Maximum 3 credits for achieving the prescribed lighting performance in each type of not normally occupied areas, regarding the illuminance and lighting quality as listed below: i. Maintained illuminance and illuminance uniformity; ii. Achieving the limiting unified glare rating; and iii. Light sources with an appropriate colour rendering index. | None. | 3 | Y
IEQ 12 | Background Noise | 1 credit for demonstrating background noise levels from both external sources and building services equipment are within the prescribed criteria. | Buildings/ premises which are inherently noisy. | 1 | Y
IEQ 13 | Room Acoustics | 1 credit for demonstrating that the mid-frequency reverberation time in applicable rooms meets the prescribed criteria of different types of premises. | Buildings/ premises where speech intelligibility is not important, and rooms of a special acoustical nature. | 1 | Y
IEQ 14 | Noise Isolation | 1 credit for demonstrating airborne noise isolation between rooms, spaces and premises fulfils the prescribed criteria. | Buildings/ premises which are inherently noisy and unaffected by noise. | 1 | Y | 0
|  | For residential developments only, 1 Bonus credit for demonstrating impact noise isolation between floors fulfils the prescribed criteria. | None. | 1B | Y |  | B
IEQ 15 | Vibration | 1 Bonus credit for vibration levels not exceeding the prescribed criteria. | None. | 1B | Y |  | B
Credit Applicable: |  |  |  |  | 26+5B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
Innovations And Additions (IA) |  |  |  | 12B | Y/N? | 0
IA 1 | Innovative Techniques | Maximum 5 Bonus credits for implementation of each innovative technique which provides environmental benefits in addition to those already covered in the Manual. | None. | 5B | Y |  | B
IA 2 | Performance Enhancements | Maximum 5 Bonus credits for having exemplary performance of the requirement stipulated in the Manual. | None. |  | Y |  | B
IA 3 | Provision of Venues or Public Spaces for Environmental Programme | Credit Requirement 1 Bonus credit for providing venue or public spaces for environmental programmes or events. | None. | 1B | Y |  | B
IA 4 | Engagement with Neighbourhoods | 1 Bonus credit for planning, managing and conducting a significant and wide ranging social engagement, engaging the impacted and relevant constituents in the community. | None. | 1B | Y |  | B
IA 5 | Provision of Electrical Vehicle Charging Stations | 1 Bonus credit for providing quick charger(s) for Electric Vehicles (EVs) for 50% of the total parking capacity of the site. | None. | 1B | Y |  | B
IA 6 | Recognition and Appreciation Awarded from Other Organisations | Maximum 2 Bonus credits for obtaining/ achieving the following listed environmental award/ certification scheme/ campaign. i. EarthCheck Certification; ii. Green Building Award; iii. Green Globe Certification; iv. CLP GreenPLUS Award; v. Hong Kong Awards for Environmental Excellence (HKAEE) “Sectoral Awards”; vi. Hong Kong Green Mark Certification Scheme; vii. Sustainable Building Index; viii. Voluntary Building Assessment Scheme (VBAS) – Environmental Awareness Quality Label; and ix. Other green building related award/ certification scheme/ campaign which is not listed above. | None. | 2B | Y |  | B
IA 7 | Achievement of Hong Kong Green Organisation Certification | Maximum 2 Bonus credits for obtaining the following certificate(s) of Hong Kong Green Organisation Certification (HKGOC): i. Wastewi$e Certificate; ii. Energywi$e Certificate; iii. IAQwi$e Certificate; and iv. Carbon Reduction Certificate. | None. | 2B | Y |  | B

## Results
Category | Applicable Credits (A) | Achieved Credits (B) | % Achieved credit (C) | Category Weighting (D) | Weighted Achieved Score (E) | Category Grade |  | Grade | Overall | MAN | SA | MWA | EU | WU | IEQ
Management (MAN) | 23 | 0 | 0% | 24% | 0 | No Rating | 1 | Platinum | 75 | 70% | 50% | 50% | 70% | 50% | 50%
Site Aspects (SA) | 22 | 0 | 0% | 10% | 0 | No Rating | 1 | Gold | 65 | 60% | 40% | 40% | 60% | 40% | 40%
Materials and Waste Aspects (MWA) | 17 | 0 | 0% | 14% | 0 | No Rating | 1 | Silver | 55 | 50% | 30% | 30% | 50% | 30% | 30%
Energy Use (EU) | 39 | 0 | 0% | 24% | 0 | No Rating | 1 | Bronze | 40 | 40% | 20% | 20% | 40% | 20% | 20%
Water Use (WU) | 23 | 0 | 0% | 14% | 0 | No Rating | 1
Indoor Environmental Quality (IEQ) | 26 | 0 | 0% | 14% | 0 | No Rating | 1
Innovations And Additions (IA) |  | 0 |  |  | 0
Sub-rating |  |  |  |  | 0 | No Rating | 1
Overall rating |  |  |  |  | Uncertified |  | 1