## Detail (EDC V1.0)
BEAM Plus Existing Data Centres (Version 1.0) Credit Summary
BEAM Plus Project No:
Project Name:
Comprehensive Scheme A / B :
1. | Project Description:
2 | Submission Schedule: (applicable to Comprehensive Scheme B only)
|  | 1st Submission: | MAN / IDCM/ SS / MW/ EU/ WU/ HWB/ IA *
|  | 2nd Submission: | MAN / IDCM/ SS / MW/ EU/ WU/ HWB/ IA *
|  | ____ Submission: | MAN / IDCM/ SS / MW/ EU/ WU/ HWB/ IA *
Final Submission
* Please delete as appropriate

## Credit Checklist
2. Credit Summary
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Management (MAN) |  |  |  | 15+3B | Y/N?
MAN-00-P1 | Green Purchasing Plan | Demonstrate that green purchasing plan and procedures (including both materials and services) either follow their internal company guideline or other international standards, shall be in place. | All DC | Required | Y | Required
MAN-01-01 | EHS and Energy Management System | 1 credit point where the DC management operates an Environmental Management System (EMS) certified to ISO 14001. | All DC | 1 | Y | 0
|  | 1 credit point where the DC management operates an Occupational Health and Safety System (OHSAS). |  | 1 | Y | 0
|  | 1 credit point where the DC management operates an Energy Management System. |  | 1 | Y | 0
|  | 1 Bonus credit point where DC management operates an OHSAS certified to ISO 45001. |  | 1B | Y | 0 | B
|  | 1 Bonus credit point where the DC management operates an EnMS certified to ISO 50001. |  | 1B | Y | 0 | B
MAN-02-01 | Environmental, Social and Governance (ESG) Disclosure | (a) Disclosure of Sustainability Policy and Target 1 credit point where the DC Owner/ DC Management Company discloses sustainability policy and targets to the public. | All DC | 1 | Y | 0
|  | (b) ESG Reporting 1 Bonus credit point where the Building Owner/ Building Management Company follows Global Reporting Initiative (GRI) Sustainability Reporting Standards and discloses the G4 sustainability report to the public. |  | 1B | Y | 0 | B
MAN-03-01 | Staff Training and Resources | (a) Staff and Technical Resources 1 credit point for having adequate staff and technical resources to meet the O&M requirements of the DC. | All DC | 1 | Y | 0
|  | (b) Staff Training 1 credit point for providing adequate and periodic training for the staff responsible for the O&M of the DC. |  | 1 | Y | 0
MAN-03-02 | Building and Site Operation and Maintenance | (a) DC Building Maintenance 1 credit point for demonstrating the operation of a planned programme of regular inspection, cleaning and maintenance of the DC building’s fabric and structure under the control of the Applicant. | Part (a) - All DC with building’s fabric and structure that are controlled by the Applicant. | 1 | Y | 0
|  | (b) External Areas and Facilities 1 credit point for demonstrating the operation of a planned programme of regular inspection, cleaning and maintenance of external areas and facilities. | Part (b) - All DC with external areas and facilities that are controlled by the Applicant | 1 | Y | 0
IDCM-03-03 | Building Services Operation and Maintenance | (a) Central Heating Ventilation and Air-Conditioning (HVAC) Plant 2 credit points for demonstrating the operation of a planned programme of regular inspection and maintenance of the central HVAC plant. | All DC | 2 | Y | 0
|  | (b) Other Engineering Systems Maximum 4 credit points for demonstrating the operation of a planned programme of regular inspection and maintenance of the following listed systems: i. Air-conditioning system except HVAC plant; ii. Electrical system; iii. Lighting system; and iv. Plumbing and drainage system. |  | 4 | Y | 0
|  | (c) Assessment of Operation & Maintenance Practice 1 credit point for having undertaken an audit of the effectiveness of the O&M practices for all building services engineering systems. |  | 1 | Y | 0
|  |  |  | Credit Applicable: | 15
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Integrated Design & Construction Management (IDCM) |  |  |  | 9+17B | Y/N?
IDCM-00-P1 | Sustainability Champions - Project | Prerequisite achieved for demonstrating that an accredited BEAM Professional (BEAM Pro) with a valid credential for BEAM Plus Existing Data Centres is engaged as the Project BEAM Pro of the consultant team. | All DC | Required | Y | Required
IDCM-00-P2 | Environmental Management Plan | This Prerequisite is not applicable under BEAM Plus EDC.
IDCM-00-P3 | Timber Used for Temporary Works | This Prerequisite is not applicable under BEAM Plus EDC.
IDCM-01-01 | Sustainability Champions - Design | (a) BEAM Accredited Personnel 1 credit point for having at least 2 members from the on-site team are an accredited BEAM Professional with EDC credential, with the members employed with the building management team for at least 6 months prior to the time of first assessment submission. Alternatively, 1 credit point for at least 1 key member from the Building Management Company is an accredited BEAM Professional with EDC credential and at least 1 member is an accredited BEAM Affiliate, with such members employed with the DC building management team for at least 6 months prior to the time of first assessment submission. | All DC | 1 | Y | 0
|  | (b) Professionally Qualified Building Manager 1 credit point for the DC building-in-charge being an accredited BEAM Professional with EDC credential and with at least 1 professional corporate membership qualification (e.g. HKIH, HKIA, HKIE, HKIS (BS/PFM), RICS (BS/FM), IFMA, HKIFM, BSOMES, or equivalent). |  | 1 | Y | 0
IDCM-01-02 | Complimentary Certification | (a) BEAM Plus Neighbourhood (ND) 1 Bonus credit point where the Project is certified by BEAM Plus Neighbourhood (ND) certification. | All DC | 1B | Y | 0 | B
|  | (b) (b) BEAM Plus New Buildings/ New Data Centres (NB/ NDC) 1 Bonus credit point where the project is certified by BEAM Plus New Buildings (NB)/ New Data Centres (NDC) certification. |  | 1B | Y | 0 | B
|  | (c) BEAM Plus Interiors (BI) 1 Bonus credit point for preparing the Project for BEAM Plus Interiors (BI) certification. |  | 1B | Y | 0 | B
IDCM-01-03 | Integrated Design Process | 1 credit point for providing at least 3 of the listed amenities that improve the operation and maintenance of the building and its engineering services. | All DC | 1 | Y | 0
IDCM-01-04 | Life Cycle Costing | This credit head is not applicable under BEAM Plus EDC.
IDCM-01-05 | Commissioning | (a) Planning and Investigation 1 Bonus credit point for planning the retro-commissioning (RCx) process and identifying the potential energy saving opportunities (ESOs). | All DC | 1B | Y | 0 | B
|  | (b) Implementation 1 o 3 Bonus credit points for implementing the selected ESOs for each of the following systems: i. Air-conditioning system; ii. Electrical system; iii. Lift and escalator (if any) system; and iv. Plumbing and drainage system. |  | 3B | Y | 0 | B
|  | (c) On-going Commissioning 1 to 3 Bonus credit points for executing on-going commissioning for each of the following systems: i. Air-conditioning system; ii. Electrical system; iii. Lift and escalator (if any) system; and iv. Plumbing and drainage system. |  | 3B | Y | 0 | B
|  | (d) RCx Professional 1 Bonus credit point for engaging an accredited RCx Professional to carry out the RCx process. |  | 1B | Y | 0 | B
IDCM-02-01 | Sustainability Champions - Construction | This credit head is not applicable under BEAM Plus EDC.
IDCM-02-02 | Measures to Reduce Site Emissions | This credit head is not applicable under BEAM Plus EDC.
IDCM-02-03 | Construction and Demolition Waste Recycling | (a) Renovation Waste Management Plan 1 credit point for developing a Renovation Waste Management Plan for renovation. | All DC | 1 | Y | 0
|  | (b) Renovation Waste Recycling 1 credit point for demonstrating compliance with the Renovation Waste Management Plan and the application of proactive waste management provisions during construction (demolition and construction); and recycling of at least 15% of construction waste (demolition and construction). |  | 1 | Y | 0
IDCM-02-04 | Construction IAQ Management | (a) Construction Indoor Air Quality (IAQ) Management Plan 1 credit point for providing a Construction Indoor Air Quality (IAQ) Management Plan. | All DC | 1 | Y | 0
|  | (b) Implementation of Construction Indoor Air Quality (IAQ) Management Plan 1 credit point for providing records that the Construction IAQ Management Plan has been implemented by the DC Owner/ DC Management Company/ tenants during renovation. | All DC | 1 | Y | 0
IDCM-02-05 | Considerate Construction | This credit head is not applicable under BEAM Plus NDC.
IDCM-02-06 | Building Management Manual | 1 credit point for providing a fully documented Operations and Maintenance Manual and Energy Management Manual. | All DC | 1 | Y | 0
IDCM-02-07 | Operator Training plus Chemical Storage Room | 1 credit point for providing training for operations and maintenance staff to the minimum specified; and demonstrating that adequate maintenance facilities are provided for chemical storage and mixing. | All DC | 1 | Y | 0
IDCM-03-01 | Digital Facility Management Interface | 1 Bonus credit point for providing a digital interface in addition to the project design metering provision for future DC facility management team to review the building operation performance. | All DC | 1B | Y | 0 | B
IDCM-03-02 | Occupant Engagement Platform | 1 Bonus credit point for providing a digital platform to engage building occupants. | All DC | 1B | Y | 0 | B
IDCM-03-03 | Document Management System | 1 Bonus credit point for operating an electronic O&M platform by the DC Owner/ DC Management Company. | All DC | 1B | Y | 0 | B
IDCM-03-04 | BIM Integration | 1 Bonus credit point for BIM application for Facility Management Use. | All DC | 1B | Y | 0 | B
IDCM-04-01 | Design for Engagement and Education on Green Buildings | 1 to 2 Bonus credit points for providing any two (2) or four (4) education elements to advocate the behavioural change of DC building users. i. Provide users with manuals for all green building design measures and provisions. ii. Provide educational signage system that is integrated with the major communal areas of the project to educate users and visitors about the benefits of the green building design measures and provisions. iii. Provide users a platform for sustainable living showcase demonstration, experience or sharing that are relevant to the enabling design measures and provisions in the project. e.g. websites, regular publications available to the public, newspapers or other means. iv. Organise educational seminar/ promotion campaign; v. Arrange workshop for DC building users to read through and review the building user guide/ manuals; vi. Promote or participate in Hong Kong Green Building Week organised by Constriction Industry Council (CIC) and the Hong Kong Green Building Council Limited (HKGBC); and vii. Additional or alternative education element(s) proposed by the Applicant with substantiation demonstrating strategies compatible with the listed strategies for achieving the credit objective. | All DC | 2B | Y | 0 | B
|  |  |  | Credit Applicable: | 9
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Sustainable Site (SS) |  |  |  | 8+8B | Y/N?
SS-00-P1 | Minimum Landscaping Requirements | This Prerequisite is not applicable under BEAM Plus NDC.
SS-01-01 | Pedestrian-oriented and Low Carbon Transport | (a) Accessibility to Public Transport 1 credit point for achieving Accessibility Index of 15 or more for all buildings of a development. | All DC | 1 | Y | 0
|  | (b) Pedestrian-oriented Access 1 credit point for achieving 50% or more of the pedestrian-oriented transport planning measures. |  | 1 | Y | 0
|  | 1 additional Bonus credit point for 100% achievement. |  | 1B | Y | 0 | B
|  | (c) Cycling Facilities and Network Integration 1 Bonus credit point for providing cycling facilities within the Site and integrating with the public cycling network if a public cycling network exists or has been planned nearby. |  | 1B | Y | 0 | B
|  | (d) Charging Facilities for Electric Vehicle (EV) 1 Bonus credit point for providing EV medium chargers for at least 50% of all parking spaces and EV charging-enabling for all parking spaces (including visitor car parks). |  | 1B | Y | 0 | B
SS-01-02 | Neighbourhood Amenities | 1 credit point where adequate amenities for building users are located within the site or 1,000m walking distance/ an equivalent horizontal commuting time from the site entrance(s). | All DC | 1 | Y | 0
SS-01-03 | Building Design for Sustainable Urbanism | This credit head is not applicable under BEAM Plus EDC.
SS-01-04 | Neighbourhood Daylight Access | This credit head is not applicable under BEAM Plus EDC.
SS-01-05 | Noise Control for Building Equipment | (a) Provision of Acoustic Treatment 1 credit point for providing adequate acoustic treatment to the following building services equipment: chillers, cooling towers, ventilation fans with Sound Power Level (SWL) higher than 80 dB(A). | All DC | 1 | Y | 0
|  | (b) Demonstration of Compliance with HKPSG Criteria 1 credit point for demonstrating that the level of the intruding noise at the façade of the potential Noise Sensitive Receivers (NSRs) is in compliance with the criteria recommended in the Hong Kong Planning Standards and Guidelines (HKPSG). |  | 1 | Y | 0
SS-02-01 | Light Pollution Control | 2 credit points if there are no external lightings installed for the DC building. Alternatively, • 1 credit point for switching off the DC Owner, DC Management Company’s and tenants’ (if any) external lightings from 23:00 to 07:00. | All DC | 2 | Y | 0
SS-02-02 | Biodiversity Enhancement | This credit head is not applicable under BEAM Plus EDC.
SS-03-01 | Urban Heat Island Mitigation | (a) Mitigation Strategy at Primary Zone 1 to 2 Bonus credit points for demonstrating the implementation of any combination of the following strategies for a minimum of 10% or 20% of the external non-roof area (i.e. ground floor and podium with less than 15m in height): i. Greenery; ii. Water feature; iii. Green wall or vertical greening; iv. Shading device; and/or v. Paving materials with solar reflectance (SR) of 0.33. | Whole building DC developments | 2B | Y | 0 | B
|  | (b) Green Roof 1 Bonus credit point for providing green roof and/ or organic farm for at least 20% of the available main roof area. |  | 1B | Y | 0 | B
SS-03-02 | Immediate Neighbourhood Wind Environment | This credit head is not applicable under BEAM Plus EDC.
SS-03-03 | Outdoor Thermal Comfort | This credit head is not applicable under BEAM Plus EDC.
SS-04-01 | Stormwater Management | 1 Bonus credit point for demonstrating that adequate stormwater management measures have been provided to cater the total volume of runoff for one hour corresponding to a design rainfall of at least 30mm/event for the site in its post-developed conditions. | Whole Building DC Developments with a site area of 1,000m2 or more. | 1B | Y | 0 | B
SS-04-02 | Design for Climate Change Adaptation | 1 BONUS credit for studying the projected variation in temperature and rainfall and water level rise/ storm surge of adjacent water bodies due to climate change and its impact on the development, and prepare mitigation proposal to improve the climate resilience of the DC. | Whole building DC developments | 1B | Y | 0 | B
|  | 1 additional Bonus credit point for including quantitative calculation to support the resilience design which is technically eligible and cost effective. |  | 1B | Y | 0 | B
|  |  |  | Credit Applicable: | 7
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Materials and Waste (MW) |  |  |  | 12+15B | Y/N?
MW-00-P1 | Minimum Waste Handling Facilities | For Whole Buildings DC Developments: Providing spaces for collection, sorting, storage and disposal of waste and recovered materials. For DC Developments located in part of building: Providing storage facilities at prominent location for the collection of paper, plastic and metal waste. | All DC | Required | Y | Required
MW-01-01 | Building Re-use | This credit head is not applicable under BEAM Plus EDC.
MW-01-02 | Modular and Standardised Design | This credit head is not applicable under BEAM Plus EDC.
MW-01-03 | Prefabrication | This credit head is not applicable under BEAM Plus EDC.
MW-01-04 | Design for Durability and Resilience | This credit head is not applicable under BEAM Plus EDC.
MW-02-01 | Sustainable Forest Products | This credit head is not applicable under BEAM Plus EDC.
MW-02-02 | Recycled Materials | This credit head is not applicable under BEAM Plus EDC.
MW-02-03 | Ozone Depleting Substances | (a) Newly Installed and Existing Equipment using Refrigerants 1 credit point for all the equipment (both newly purchased and existing) using the refrigerants with Global Warming Potential (GWP) ≤ 1,900. Alternatively, • For equipment with refrigerant GWP value > 1,900, credit point can be achieved when the Applicant can demonstrate a phased programme of refrigerant replacement. | All Building Equipment & insulation servicing the Assessed DCs. | 1 | Y | 0
|  | 1 credit point for using refrigerants with a combined value less than or equal to the threshold for the combined contributions to ozone depletion and global warming potentials for all new and existing HVAC&R equipment that under the control of Applicant. |  | 1 | Y | 0
|  | (b) Fire Suppression and Other Materials 1 credit point for using the fire suppression and other materials that avoids the use of ozone depleting substances in their manufacture, composition or use. |  | 1 | Y | 0
MW-02-04 | Regional Materials | This credit head is not applicable under BEAM Plus EDC.
MW-02-05 | Use of Green Products | (a) Materials Purchasing Practices 1 credit point for demonstrating at least 50% of purchased on-going consumables are environmentally friendly products for the past 12 months as minimum. | All DC | 1 | Y | 0
|  | 1 credit point for demonstrating at least 50% of purchased durable goods are environmentally friendly products for the past 12 months as minimum. |  | 1 | Y | 0
|  | 1 credit point for demonstrating at least 70% of purchased both on-going consumables and durable goods are environmentally friendly products for the past 12 months. |  | 1 | Y | 0
|  | 1 Bonus credit point for demonstrating at least 70% of purchased both on-going consumables and durable goods are environmentally friendly products for the past 24 months. |  | 1B | Y |  | B
|  | (b) Use of Green Products Maximum 2 Bonus credit points for purchasing green products certified by Construction Industry Council (CIC) Green Product Certification or other internationally recognised schemes. |  | 2B | Y |  | B
MW-02-06 | Life Cycle Assessment | This credit head is not applicable under BEAM Plus EDC.
MW-03-01 | Adaptability and Deconstruction | This credit head is not applicable under BEAM Plus EDC.
MW-03-02 | Enhanced Waste Handling Facilities | (a) Waste Management Plan 1 credit point for developing a waste management plan. | All DC | 1 | Y | 0
|  | (b) Enhanced Waste Handling Facilities 1 credit point for providing at least 3 of the following listed on-site recycling facilities and implementing the recyclable materials collection arrangement: i. IT related waste such as, electronic equipment; ii. Plastic recyclable; iii. Metal recyclable; iv. Glass recyclable; v. Paper recyclable; vi. Food waste; vii. Organic landscape waste; and viii. Beverage carton recyclable. |  | 1 | Y | 0
MW-04-01 | Best Practice on Material Usage | 2 credit points for demonstrating the adoption of at least 4 best practices relating to the efficient use of materials as mentioned in the Green Data Centre Practice Guide published by BEAM Society Limited (BSL). | All DC | 2 | Y | 0
|  |  |  | Credit Applicable: | 10
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Energy Use (EU) |  |  |  | 35+3B | Y/N?
EU-00-P1 | Minimum Energy Performance | Conducting energy audit in accordance with the Buildings Energy Efficiency Ordinance (Cap 610) requirements. | All DC | Required | Y | Required
EU-01-01 | Low Carbon Passive Design | This credit head is not applicable under BEAM Plus EDC.
EU-01-02 | Reduction of CO2 Emissions | This credit head is not applicable under BEAM Plus EDC.
EU-01-03 | Peak Electricity Demand Reduction | This credit head is not applicable under BEAM Plus EDC.
EU-01-04 | Metering and Monitoring | (a) Meters for Electrical Loads 1 credit point for sub-metering systems for the following electrical loads where applicable: i. Central AC plant - Water Side; ii. Central AC plant - Air Side; and iii. Lighting. | All DC | 1 | Y | 0
|  | (b) BMS Logging 1 credit point for having Building Management System (BMS) to log operation data (e.g. pressure, temperature, flow rate, on/ off status) for monitoring operation and function of the system including the following as a minimum: i. Central AC plant - Water side; ii. Central AC plant - Air side; iii. Cooling load; and iv. Lighting control. |  | 1 | Y | 0
|  | (c) PUE Monitoring 1 credit point for energy metering to provide total facility power and energy usage and total IT equipment power and energy at each output of Power Distribution Unit (PDU) for determining instantaneous and average Power Usage Effectiveness (PUE) data. |  | 1 | Y | 0
EU-02-01 | Renewable and Alternative Energy Systems | (a) Solar Energy Feasibility Study 1 credit point for evaluating the building roof’s potential for harnessing solar energy. | All DC | 1 | Y | 0
|  | (b) Renewable Energy Application 1 Bonus credit point where at least 0.2% of DC energy consumption in communal area is obtained from renewable energy sources. |  | 1B | Y | 0 | B
EU-03-01 | Air-Conditioning Units | This credit head is not applicable under BEAM Plus EDC.
EU-03-02 | Clothes Drying Facilities | This credit head is not applicable under BEAM Plus EDC.
EU-03-03 | Energy Efficient Appliances | (a) Use of Efficient UPS 1 credit point for demonstrating that the Uninterruptible Power Supplies (UPS) is procured in accordance with certified energy efficient products scheme. | All DC | 1 | Y | 0
|  | (b) Use of Sustainable IT Equipment 1 credit point for demonstrating that the IT Equipment for the running and operating of the DC of is procured in accordance with certified energy efficient products scheme. | DC with operational control over the IT Equipment. | 1 | Y | 0
EU-03-04 | Cooling System Efficiency | This credit head is not applicable under BEAM Plus EDC.
EU-03-05 | Air Management System | (a) Air Management System 1 credit point for demonstrating the total air flow efficiency in all data halls, from supply to return, is of 0.9 kW/m3/s. | All DC | 1 | Y | 0
|  | (b) Data Hall Supply Air Temperature Control 1 credit point for demonstrating the data hall supply air temperature is 24 °C or above. |  | 1 | Y | 0
EU-04-01 | Best Practice on Energy Use | (a) Best Practices for Major Controls 1 to 3 credit points for incorporating at least 2 best practices under each of the following aspect in the Green DC Practice Guide published by BEAM Society Limited: i) Cooling System; ii) Air Flow Management; iii) Operating at Higher Temperature and Humidity; iv) Cooling Management; and v) Power System. | All DC | 3 | Y | 0
|  | (b) Best Practices for Other Controls 2 credit points for incorporating at least 6 best practices across the following aspects as listed in the Green DC Practice Guide published by BEAM Society Limited: i) Design of Resilience; ii) Monitoring and Managing Energy Efficiency; iii) IT Equipment Deployment; iv) IT Application System and IT Service Deployment; and v) Telecommunications and Network Cabling. |  | 2 | Y | 0
EU-04-02 | Energy Management | (a) Energy Management Policy 1 credit point for an energy management policy endorsed by top management. | All DC | 1 | Y | 0
|  | (b) Energy Saving Target 1 to 2 credit points for energy management plan covering less than 3 year/ 3 years or more, respectively. |  | 2 | Y | 0
|  | (c) Energy Action Plan 1 to 2 credit points for energy action plan covering less than 3 year/ 3 years or more, respectively. |  | 2 | Y | 0
|  | (d) Appointment of Energy Warden 1 credit point for appointing an Energy Warden in the DC Management Company. |  | 1 | Y | 0
EU-04-03 | Energy Analysis | (a) Data Collection Record 1 to 2 credit point(s) for providing energy consumption data record of at least 1 year/ more than 3 years for major electrical loads. | All DC | 2 | Y | 0
|  | (b) Data Analysis 1 credit point for calculating the EUI of the following services in data analysis: i) Air-conditioning system; and ii) Lighting. |  | 1 | Y | 0
|  | 1 credit point for calculating and recording the PUE (Level 2) for 1 year. |  | 1 | Y | 0
|  | (c) Energy Audit Report 2 credit point for filling up the entire Template 1 on Additional Information to Executive Summary of Energy Audit Report. |  | 2 | Y | 0
|  | (d) Carbon Audit Report 1 credit point for conducting carbon audit in accordance with the requirements as stipulated in the guideline issued by the Authority. |  | 1 | Y | 0
EU-05-01 | Energy Benchmarking and System Improvement | Credit point(s) can be achieved based on the Operating PUE value | All DC | 8 | Y | 0
|  | Bonus credit point(s) can be achieved based on the Operating PUE value |  | 2B | Y | 0 | B
EU-05-02 | Enhancement | (a) Research and Development in Energy 1 Bonus credit point for conducting research and development or participating in competition with published paper related to energy aspects for DCs | All DC | 1B | Y | 0 | B
|  | (b) Compliance with the BEC 1 to 4 Bonus credit points for compliance with the latest version of the following listed: i) Energy Efficiency Requirements for Air-Conditioning Installations; ii) Energy Efficiency Requirements for Electrical Installations; iii) Energy Efficiency Requirements for Lighting Installations; and/or iv) Energy Efficiency Requirements for Lift and Escalator Installations. |  | 4B | Y | 0 | B
|  | (c) Separate Energy Charges 1 Bonus credit point where separate charges are made for energy use. |  | 1B | Y | 0 | B
|  | (d) Other Approaches 1 to 6 Bonus credit points for adopting other energy conservation approaches not prescribed above. |  | 6B | Y | 0 | B
|  |  |  | Credit Applicable: | 34
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Water Use (WU) |  |  |  | 12+2B | Y/N?
WU-00-P1 | Minimum Water Saving Performance | This prerequisite is not applicable under BEAM Plus NDC.
WU-01-01 | Annual Water Use | Credit point(s) can be achieved based on the estimated aggregate annual saving by the use of water efficient devices. | All DC | 4 | Y | 0
WU-01-02 | Water Efficient Irrigation | This credit head is not applicable under BEAM Plus EDC.
WU-01-03 | Water Efficient Appliances | This credit head is not applicable under BEAM Plus EDC.
WU-01-04 | Water Leakage Detection | 1 Bonus credit point for installing water leakage detection systems in all data halls and all municipal potable water tank rooms (if applicable) | All DC | 1B | Y | 0 | B
WU-01-05 | Twin Tank System | 1 Bonus credit point for providing twin tank for either potable or flushing water supply system. 2 Bonus credit points for providing twin tank for both potable and flushing water supply system. | All DC (including DC with centralised/ shared tank that is outside the assessment boundary) | 2B | Y | 0 | B
WU-01-06 | Cooling Tower Water | 1 credit point for reducing fresh water consumption by installing water treatment system which can achieve minimum 7 cycles of concentration with acceptable water quality. | All DC with cooling tower using potable water as make up water | 1 | Y | 0
|  | 1 additional BONUS credit point for 8 or more cycles of concentration with acceptable water quality. |  | 1B | Y | 0 | B
WU-02-01 | Effluent Discharge to Foul Sewers | (a) Water Closets 1 credit point for installing dual flush for the water closets. | All DC | 1 | Y | 0
|  | (b) Urinals 1 credit point for installing urinals with WELS Grade 2 or above. |  | 1 | Y | 0
WU-03-01 | Water Harvesting and Recycling | 1 or 2 Bonus credit points for harvesting rainwater and/ or recycling grey water that leads to a reduction of at least 2.5% or 5% in the consumption of potable water. | All DC | 2B | Y | 0 | B
WU-04-01 | Smart Water Metering | 1 credit point for demonstrating the provision of permanent smart water meter for cooling towers water use and indoor plumbing fixtures and fitting, and at least 2 of the other water systems which are able to display metered data, treading of water consumption and relevant parameters. | All DC with more than one water system | 1 | Y | 0
WU-04-02 | Water Saving Management | Credit point(s) can be achieved based on the reduction percentage by comparing water bill/ metering data. (Reference year can be any year in the past 5 years). | All DC | 4 | Y | 0
|  |  | All DC | 1B | Y | 0 | B
|  |  |  | Credit Applicable: | 12
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Health and Wellbeing (HWB) |  |  |  | 15+6B | Y/N?
HWB-00-P1 | Minimum Ventilation Performance | (a) On-site Outdoor Air Quality To measure outdoor air pollutants at selected intake location(s). (b) Minimum Ventilation To demonstrate the project is in compliance with the minimum ventilation quantity in accordance with of ANSI/ASHRAE Standard 62.1-2019. Alternatively, • In case of the minimum ventilation rate of ANSI/ASHRAE Standard 62.1-2019 is not complied due to the physical constraints of the existing ventilation system, demonstrate that the system is operated at maximum outdoor air delivery rate and provide not less than 5 l/s per person of combined outdoor air rate. | All DC | Required | Y | Required
HWB-01-01 | Healthy and Active Living | 1 Bonus credit point for scoring at least 3 items of all applicable design measures for healthy and active living. | All DC | 1B | Y | 0 | B
HWB-01-02 | Biophilic Design | This credit head is not applicable under BEAM Plus EDC.
HWB-02-01 | Inclusive Design | 1 credit point for providing at least 3 applicable enhanced provisions as stipulated in the “Recommended Design Requirements” of BFA 2008. | All DC | 1 | Y | 0
HWB-03-01 | Enhanced Ventilation | (a) Fresh Air Provision 1 credit point for demonstrating that 90% of not normally occupied spaces in the DC are provided with adequate ventilation. | All DC | 1 | Y | 0
|  | (b) Exhaust Air 1 credit point for the provision of an effective ventilation system for spaces where significant indoor pollution sources are generated. |  | 1 | Y | 0
HWB-03-02 | Waste Odour Control | This credit head is not applicable under BEAM Plus NDC.
HWB-03-03 | Acoustic and Noise | (a) Background Noise in Data Hall 1 credit point for demonstrating the internal noise levels at data hall areas are maintained at an appropriate level. | All DC | 1 | Y | 0
|  | (b) Room Acoustics 1 credit point for demonstrating that the mid-frequency reverberation time in applicable rooms meets the prescribed criteria of different types of premises. |  | 1 | Y | 0
|  | © Noise Isolation 1 credit point for demonstrating airborne noise isolation between rooms, spaces and premises fulfils the prescribed criteria. |  | 1 | Y | 0
HWB-03-04 | Indoor Vibration | 1 credit point for demonstrating vibration levels not exceeding the prescribed criteria. | All DC | 1B | Y | 0 | B
HWB-03-05 | Indoor Air Quality | 1 to 2 credit points for submitting a valid IAQ Certification Scheme, Good Class or Excellent Class certificate issued by the Environmental Protection Department (EPD) covering the whole DC. | All DC | 2 | Y | 0
HWB-03-06 | Thermal Comfort | (a) Temperature Profile in Data Hall 1 credit point for sustaining the air temperature at the design value within ±2.0°C when the air side system is operating at steady state under normal operation periods. | All DC | 1 | Y | 0
|  | (b) Thermal Comfort in Normally Occupied Spaces 1 credit point for demonstrating an appropriate temperature (i.e. ≤25.5°C), relative humidity (i.e. ≤70%) and air velocity (≤0.3 m/s) in normally occupied spaces. |  | 1 | Y | 0
HWB-03-07 | Artificial Lighting | (a) Artificial lighting in Data halls 1 credit point for achieving the prescribed lighting performance in Data halls. | All DC | 1 | Y | 0
|  | (b) Artificial lighting in normally occupied spaces, not normally occupied spaces and unoccupied spaces 1 credit point for achieving the prescribed lighting performance in normally occupied spaces, not normally occupied spaces and unoccupied spaces. |  | 1 | Y | 0
HWB-03-08 | Daylight | This credit head is not applicable under BEAM Plus EDC.
HWB-03-09 | Biological Contamination | 1 credit point for complying with the recommendations given in the Code of Practice for Prevention of Legionnaires’ Disease 2021 Edition in respect of Water Supply Systems, HVAC Systems and other Water Features. | All DC | 1 | Y | 0
|  |  |  | Credit Applicable: | 13
|  |  |  | Credit Anticipated: | 0
|  |  |  | Bonus Anticipated: | 0 |  | B
|  |  |  | Percentage of Credits Achieved: | 0%
| Section | Credit Requirement | Extent of Application | Credit Attainable | Credit Applicable | Credit Anticipated
Innovations and Additions (IA) |  |  |  | Max. 10 Bonus | Y/N?
IA-01-01 | Innovations and Additions | Present evidence of the application of new practices, technologies and/ or techniques that are (1) not described in this Manual; or (2) not market mainstream implementation; or (3) multiple aspect achievement; and the associated benefits in addressing sustainability objectives for existing DCs | All DC | 10B | Y | 0 | B

## Project Score Result
Category | Applicable Credits (A) | Achieved Credits (B) | % of Achieved Credit (C) | Category Weighting (D) | Weighted Achieved Score (E)
Management (MAN) | 15 | 15+0B | 0% | 15% | 0%
Integrated Design & Construction Management (IDCM) | 9 | 0+0B | 0% | 15% | 0%
Sustainable Site (SS) | 7 | 0+0B | 0% | 5% | 0%
Materials and Waste (MW) | 10 | 0+0B | 0% | 55% | 0%
Energy Use (EU) | 34 | 0+0B | 0% | 40% | 0%
Water Use (WU) | 12 | 0+0B | 0% | 10% | 0%
Health and Wellbeing (HWB) | 13 | 0+0B | 0% | 10% | 0%
Innovations and Additions (IA) |  | 0B |  |  | 0%
Overall Score |  |  |  |  | 0%
Overall Rating |  |  |  |  | Prerequisite Achieved

## Pull Down List (hidden)
Defined Names | areat | ac | area | yn | prereq | prereq_b | sco_1 | sco_1_b | sco_2 | sco_2_b | sco_3 | sco_3_b | sco_5 | sco_5_b | sco_15 | sco_15_b | sco_bon | sco_bon_b | sco_6 | sco_6_b | sco_1_a | sco_2_a | sco_3_a | sco_5_a | sco_15_a | 0 | Assessment Tools | project type | rank |  |  |  |  | If
| Carpark | Central A/C | Area A |  | PR | PR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | 0 | 0 | 1 | 1 | 0 | #REF! | #REF! | #REF!
| Clubhouse | Chiller | Area B | Yes | NA | NA | NS | NS | NS | NS | NS | NS | NS | NS | NS | NS | NS | NS | NS | NS | 1 | 2 | 3 | 5 | 15 | 6 | New Data Centres Version 1.0 | Provisional Assessment (PA) | 0 | 0 | 1 | 1 | 0 | #REF! | #REF! | #REF!
| Educational | Mechnical Vent | Area C | No |  | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 5 | 5 | 15 | 15 | 1B | 1B | 6 | 6 |  | 1 | 2 | 4 | 14 | 5 |  | Preliminary Final Assessment (PFA) | 0 | 0 | 1 | 1 | 0 | #REF! | #REF! | #REF!
| Hotel | Split Type A/C | Area D |  |  |  |  | 0 | 1 | 1 | 2 | 2 | 4 | 4 | 14 | 14 |  | 0 | 5 | 5 |  |  | 1 | 3 | 13 | 4 |  | Final Assessment (FA) |  |  |  |  | 0 | #REF! | #REF! | #REF!
| Industrial | VRV | [7 empty] | 0 | 1 | 1 | 3 | 3 | 13 | 13 |  |  | 4 | 4 |  |  |  | 2 | 12 | 3 | [9 empty] | #REF!
| Residential | Windows Type A/C | [9 empty] | 0 | 2 | 2 | 12 | 12 |  |  | 3 | 3 |  |  |  | 1 | 11 | 2
| Retail | VRV & fresh air | [10 empty] | 1 | 1 | 11 | 11 |  |  | 2 | 2 |  |  |  |  | 10 | 1
|  | To be provided by future tenant | [11 empty] | 0 | 10 | 10 |  |  | 1 | 1 |  |  |  |  | 9
[15 empty] | 9 | 9 |  |  |  | 0 |  |  |  |  | 8
[15 empty] | 8 | 8 | [8 empty] | 7
[15 empty] | 7 | 7 | [8 empty] | 6
[15 empty] | 6 | 6 | [8 empty] | 5
[15 empty] | 5 | 5 | [8 empty] | 4
[15 empty] | 4 | 4 | [8 empty] | 3
[15 empty] | 3 | 3 | [8 empty] | 2
[15 empty] | 2 | 2 | [8 empty] | 1
[15 empty] | 1 | 1
0
Formulas:
rank = '[1]Summary (NB2.0)'!F29