| Credit Requirements: | - Provision of District Energy System 2 credit points are awarded where the Site is connected to a district cooling or energy system, whether there is an existing system or there will be a planned one. - District Energy System Efficiency 1 credit point is awarded if the Applicant can demonstrate that a target annual average COP of 4.7 at full utilisation can be achieved through a continuous monitoring of the plant efficiency. 1 BONUS credit point is awarded where the plant average annual efficiency (including cooling towers and primary pumps) is equal to or greater than the COP of 4.7. - Supporting Infrastructure of District Energy System 1 credit point is awarded where a walkable service tunnel with adequate maintenance access for the district system is provided. 1 BONUS credit point is awarded where other utilities services are combined with the district system piping route and a walkable service tunnel is provided. |
| --- | --- |

| Project Name: | Enter project name |
| --- | --- |
| Project Code: | Enter project code |

| Credit point(s) attainable: | 4 + 2B |
| --- | --- |
| Credit point(s) anticipated for this submission: | Enter anticipated points |

Is the project of pure residential use?

Yes or No.

Is the project a public sector project where the district energy system connection is mandated by land lease conditions or engineering conditions?

Yes or No.

- Provision of District Energy System

Where is the district energy and / or cooling system located?

Within or Outside the site

If it is provided within the Site, please provide a short summary of the feasibility study:

Click here to enter text.

Will the district plant provide at least 80% of peak cooling energy demand or equivalent for the Site after deducting the demand for residential use?

Yes or No.

- District Energy System Efficiency

Will there be a continuous monitoring of district cooling / energy plant efficiency with the target annual average COP of 4.7 at full utilisation?

Yes or No.

Will the average annual efficiency (including cooling towers and associated chilled water and condensing water pumps) have a COP equal to or greater than 4.7 at the level of the estimated annual electricity consumption and annual cooling load?

Yes or No.

- Supporting Infrastructure of District Energy System

Will there be a walkable service tunnel, with adequate maintenance access included as a part of the district energy system?

Yes or No.

If so, will other utilities services be combined with the district system piping route, together with the walkable service tunnel provided?

Yes or No.

Enclosures:

Please complete each item with a cross (☒);

- Provision of District Energy System

For a district energy and / or cooling system provided within the Site

☐	A summary of feasibility study, prepared by a suitably qualified person, demonstrating the technical and environmental viability of the district energy system for the Site.

☐	Calculation of the peak cooling energy or equivalent for the Site in accordance with the credit requirements of EA 3a.

☐ 	A scale drawing(s) on an A3 size sheet showing the location(s) of district energy plant room(s), pipe routing and other associated infrastructure.

☐ 	Other supporting document, please specify.

Describe and list other supporting documents.

For a district energy and / or cooling system provided outside the Site

☐ 	An Undertaking Letter from the owner and operator of district energy and / or cooling plant, signed by authorised signatory at director level, outlining the maximum cooling capacity and / or electrical capacity to be provided by the district system(s) to the Site.

☐ 	A scale drawing(s) on an A3 size sheet showing the locations of district energy plant, the pipe connection(s) to the Site for providing services.

☐ 	The layout plan for the district energy system substation and other associated infrastructure.

☐ 	Other supporting document, please specify.

Describe and list other supporting documents.

- District Energy System Efficiency

☐ 	An Undertaking Letter from the owner and operator of district energy and / or cooling plant, signed by authorised signatory at director level, outlining the continuous monitoring of plant efficiency with a target annual COP of 4.7 at full utilisation

☐ 	A report prepared by a suitably qualified person demonstrating that the annual average COP of district energy plant (including cooling towers and associated water and condensing water pumps) will have a COP value greater than 4.7, including the estimation of annual electricity consumption and annual cooling load.

☐ 	Other supporting document, please specify.

Describe and list other supporting documents.

- Supporting Infrastructure of District Energy System

☐ 	A scale drawing(s) on an A3 size sheet including plans and sections of the service tunnel showing the dimensions of major pipes, passages and maintenance areas etc.

☐ 	An operation plan prepared by a suitably qualified person addressing the integration of various utilities sharing a common walkable service tunnel.

☐ 	Other supporting document, please specify.

Describe and list other supporting documents.