| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All Non-residential buildings and common area of residential buildings |
| --- | --- |

| Objective | Enable building operators to measure, monitor and develop measures to improve the performance of the building's engineering systems |
| --- | --- |

| Credit Requirement | (a) Fundamental metering and monitoring 1 credit for providing energy monitoring system of equipment and system in spaces 1 BONUS for providing performance auditing monitoring system for equipment and system in spaces. (b) Metering for tenanted area 1 BONUS for allows monitoring provision of tenants’ energy consumption |
| --- | --- |

| Credit(s) Attainable | 1 + 2 BONUS |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

(a) Fundamental metering and monitoring

Please confirm that the following requirement is met by checking the box with ..

| The project is targeted to provide energy monitoring provision system of equipment and system in spaces |  |
| --- | --- |
| The project is targeted to provide performance auditing monitoring system of equipment and system in spaces |  |

Please confirm that the following requirement is met by checking the box with ..

| Monitoring Coverage (with reference to Table EU4-1 of manual) | Common area of Residential Buildings | Energy Sub-metering provision is provided for: - Each equipment in HVAC system - Lighting and small power system - Each Lift & Escalator - Each equipment in Plumbing and Drainage system |  |
| --- | --- | --- | --- |
|  | Non-Residential Buildings | Energy Sub-metering provision is provided for Landlord’s controlled area (if applicable): - Each equipment in HVAC water-side system (chiller plant, heating plant & heat rejection plant); - Each equipment in HVAC air-side system (Air handling unit); and - Each equipment in Fresh Air system (Primary air unit); - Each gas equipment in cooling or heating plant (e.g. Absorption chiller plant, centralized boiler plant) - Each equipment in Plumbing and drainage system energy consumption |  |
|  |  | Minimum one single meter for each end-use for Landlord’s controlled area (if applicable): - Variable refrigerant volume air-conditioner energy consumption; - Car park ventilation system energy consumption - Toilet exhaust ventilation system energy consumption - Lift system energy consumption; - Escalator system energy consumption; - Lighting and receptacle power energy consumption; |  |
| Sensors and Meters Requirement | Electricity metering complied with BS EN accuracy class 1 or equivalent. |  |  |
| Interval and Recording | Metering provide record at intervals of one hour or less and capable to record the item as required. |  |  |
|  | Residential Development | Records are collected monthly and be kept for at least 36 months |  |
|  | Non-residential Development | Data is transferred to a Building Management System (BMS) or other data collection system. The BMS or other data collection system should have sufficient capacity to store for at least 36 months. |  |

(b) Metering for tenanted area

Please provide the information below and confirm that the following requirement is met by checking the box with ..

| Percentage of Landlord controlled area |  | % |
| --- | --- | --- |
| Monitoring provision in Tenant area is installed | By Landlord (Path 1) By Tenant (Path 2) |  |
| The project is providing system provision (BMS or data collection facilities) to record the required data for at least 36 months; OR |  |  |
| The project is providing legally binding lease document with reference to HKGBC Green Tenancy Driver to set up the: - The Aim of improving the environmental performance - The Data sharing agreement between Landlord and Tenants - A Green Tenancy Committee (GTC) to coordinate and review the target and progress periodically |  |  |

SUBMITTALS

- Fundamental metering and monitoring

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU_4(a)_00 | BEAM Plus NB submission template for EU 4a |  |  |
| EU_4(a)_01 | Electrical schematics highlighting all locations of metering |  |  |
| EU_4(a)_02 | Control diagrams of central chiller plant monitoring system |  |  |
| EU_4(a)_03 | Specifications of all metering and measurement equipment |  |  |
|  | Catalogues of all metering and measurement equipment |  |  |
| EU_4(a)_04 | Specifications of BMS or data collection facilities |  |  |
|  | Catalogues of BMS or data collection facilities |  |  |
| EU_4(a)_05 | Schematic drawings and point schedule of BMS or data collection facilities |  |  |
| EU_4(a)_06 | Test and commissioning records |  |  |
| EU_4(a)_07 | Operation manual |  |  |

- Metering for tenanted area

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU_4(b)_01 | BEAM Plus NB submission template for EU 4b (compliance path 1 and 2) |  |  |
| EU_4(b)_02 | Electrical schematics highlighting all locations of metering (compliance path 1) |  |  |
| EU_4(b)_03 | Specifications of all metering and measurement equipment (compliance path 1) |  |  |
|  | Catalogues of all metering and measurement equipment (compliance path 1) |  |  |
| EU_4(b)_04 | Specifications of BMS or data collection facilities (compliance path 1) |  |  |
|  | Catalogues of BMS or data collection facilities (compliance path 1) |  |  |
| EU_4(b)_05 | Schematic drawings and point schedule of BMS or data collection facilities (compliance path 1) |  |  |
| EU_4(b)_06 | Test and commissioning records (compliance path 1) |  |  |
| EU_4(b)_07 | Operation manual (compliance path 1) |  |  |
| EU_4(b)_08 | Contractually binding lease document (compliance path 1 and 2) |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)