| EFB No.: | EFB-A12a |
| --- | --- |
| EFB Name.: | Control Panel Design at Lift Lobby |
| Category: | A. Mobility and Accessibility |
| Extent of Application: | Common Lifts, Escalators and Passenger Conveyors |
| Recommended Design Requirements: | Control panels or buttons at the lift lobbies should be located at 1050 mm above the finished floor level. They should be easy to operate and have a minimum luminous contrast of 30%. |
| Assessment Criteria: | - The control panels/ buttons at the lift lobbies shall be positioned at 1050 mm above the finished floor level. - The lift control panels/ buttons shall be designed such that the luminous contrast is greater than 30%. Luminous contrast means the amount of light reflected from the surface of the object compared to the amount of light reflected from the surface of its surrounding background. Such contrast expressed in percent can be determined by: [(B1-B2) / B1] x 100 Where B1 = light reflectance value (LRV) of the lighter area and B2 = light reflectance value (LRV) of the darker area. - All lift lobbies for at least one lift serving all floors, excluding those that serve only plant rooms and back-of-house areas, shall comply with the requirement. - Compliance in the fireman lift will be considered acceptable for assessment. |
| Submittals: | - EFB-A12a_01 Provide drawing(s) to identify: - The lift(s) that serving all floors. |
|  | - EFB-A12a_02 Provide any one of the supporting information: - Drawing(s) and/ or sample photo(s) to illustrate the lift control panels/ buttons with a clear and distinct contrast that is easily visible; - Calculations of the luminous contrast based on the light reflectance value (LRV) of the lift control panels/ buttons and surrounding area. |
| Reference: |  |

At least one set of photos shall be provided for each building in the project, with measurements of the relevant dimensional requirements clearly shown in the photos where applicable.