| EFB No.: | EFB-A17b |
| --- | --- |
| EFB Name.: | Lighting Design at Common Areas |
| Category: | A. Mobility and Accessibility |
| Extent of Application: | Common Areas and Facilities |
| Recommended Design Requirements: | Where additional lighting activated by sensors is provided to enhance the illumination level of the lift lobby of upper floors, corridors, accessible paths and staircases, the length of the corridors and paths and the walking speed of the elderly should be considered in setting the duration of such sensors. Alternative or stand-by light sources should be provided to illuminate any space in case of power failure. Consideration should be given to ensure gradual transition of lighting levels from one place to another. The use of natural lighting or ambient artificial white light should be encouraged. The use of wall-mounted light or peripheral lighting from floor lamps are superior to a central ceiling source as the formation of shadows can be avoided. Bare light bulbs producing glare which would cause pain to the aging eyes should be avoided. All interior spaces should be lit at a consistent and even level, from floor to ceiling and from wall to wall. High contrast between shadow and light creating confusion and disorienting patterns should be avoided. |
| Assessment Criteria: | - All common areas such as lift lobbies, corridors and staircases shall comply with the requirement. - Lighting covers shall be installed to prevent glare from bare light bulbs, avoiding discomfort or pain to aging eyes. - If lighting sensors are provided, the duration of sensors in lift lobbies, corridors, accessible paths, and staircases shall be at least 180 seconds. - Back of house staircases are excluded in the assessment. |
| Submittals: | - EFB-A17b_01 Provide drawing(s) and/ or catalogue(s) and/ or sample photo(s) to demonstrate: - The light fittings are equipped with covers to prevent glare. |
|  | - EFB-A17b_02 - Declaration signed by a representative of the Applicant (refer to Appendix A). |

At least one set of photos shall be provided for each building in the project, with measurements of the relevant dimensional requirements clearly shown in the photos where applicable.

Representative of the Applicant is defined as: (i) Building Owner; (ii) Applicant of this certification; (iii) Representative from the facility management company.