| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC |
| --- | --- |

| Objective | Encourage the use of high efficiency air distribution system to minimise the energy consumption |
| --- | --- |

| Credit Requirement | - Air Management System 1 credit point for demonstrating the total air flow efficiency in all data halls, from supply to return, is of 0.9 kW/m3/s. - Data Hall Supply Air Temperature Control 1 credit point for demonstrating the data hall supply air temperature is 24 °C or above. |
| --- | --- |

| Credit(s) Attainable | 2 |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

Please confirm that the following requirement is met by checking the box with .

| - Air Management System |  |
| --- | --- |
| The prescribed system efficiency shall be achieved at 75% of the design IT load |  |
| The calculation of air flow efficiency included both the supply and return air flows serving each data hall |  |
| Data Hall Supply Air Temperature |  |
| Measurement confirmed the data hall supply air temperature for 24 °C and above |  |

SUBMITTALS

- Air Management System

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-03-05a_00 | BEAM Plus EDC submission template for EU-03-05a |  |  |
| EU-03-05a_01 | Endorsed air flow and fan power Measurement report |  |  |
| EU-03-05a_02 | Detail Calculation for the air flow efficiency |  |  |

- Data Hall Supply Air Temperature Control

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-03-05a_00 | BEAM Plus EDC submission template for EU-03-05b |  |  |
| EU-03-05a_01 | Endorsed data hall supply air temperature Measurement report |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)