| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC |
| --- | --- |

| Objective | To enable and encourage building operators to measure, record, monitor and analyse energy performance of the building’s engineering systems, particularly concerning energy use. |
| --- | --- |

| Requirement | - Data Collection Record 1 to 2 credit point(s) for providing energy consumption data record of at least 1 year/ more than 3 years for major electrical loads. - Data Analysis 1 credit point for calculating the EUI of the following services in data analysis: - Air-conditioning system; and - Lighting. 1 credit point for calculating and recording the PUE (Level 2) for 1 year. - Energy Audit Report 2 credit points for filling up the entire Template 1 on Additional Information to Executive Summary of Energy Audit Report. - Carbon Audit Report 1 credit point for conducting carbon audit in accordance with the requirements as stipulated in the guideline issued by the Authority. |
| --- | --- |

| Credit(s) Attainable: | 7 |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

| - Data Collection Record |  |  |
| --- | --- | --- |
|  | Provide energy energy consumption data record of major electrical loads for: |  |
|  |  | at least 1 year |
|  |  | more than 3 years |
| - Data Analysis |  |  |
|  | EUI of the following services is provided: |  |
|  |  | Air-conditioning system |
|  |  | Lighting |
|  | PUE data is provided as per the following requirement: |  |
|  |  | Total facility and IT Energy consumption data for 1 year |
|  |  | Calculation of Monthly PUE for 1 year |
|  |  | The IT equipment energy are measured at all Power Distribution Units (PDUs) Output, i.e. PUE Level 2. |
| - Energy Audit Report |  |  |
|  | Completed entire Template 1 on Additional Information to Executive Summary of Energy Audit Report |  |
|  | Provide relevant calculation and/or measured data as supporting to the filled data in Template 1 |  |
|  | Report endorsed by a Registered Energy Assessor (REA) |  |
| - Carbon Audit Report |  |  |
|  | Provide a carbon audit or Greenhouse Gas (GHG) Emissions audit report in accordance with the latest Guidelines to Account for and Report on Greenhouse Gas Emissions and Removals for Buildings (Commercial, Residential or institutional Purposes) in Hong Kong, issued by Electrical & Mechanical Services Department (EMSD) and Environmental Protection Department (EPD) |  |
|  | Report shall be endorsed by a Qualified Service Provider (QSP) |  |

SUBMITTALS

- Data Collection Record

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-04-03a_00 | BEAM Plus EDC submission template for EU-04-03 |  |  |
| EU-04-03a_01 | Energy consumption data record for major electrical loads (e.g. BMS log data, metering log data, manually recorded data) |  |  |
| EU-04-03a_02 | Spreadsheet summarising the energy consumption data according to major systems with monthly bar chart plotted |  |  |

- Data Analysis

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-04-03b_00 | BEAM Plus EDC submission template for EU-04-03 |  |  |
| EU-04-03b_01 | Spreadsheet summarising EUI for the required systems |  |  |
| EU-04-03b_02 | Calculation and/ or measured data as supporting to the EUI |  |  |
| EU-04-03b_03 | Spreadsheet summarising PUE |  |  |
| EU-04-03b_04 | Calculation and/ or measured data as supporting to the PUE |  |  |

- Energy Audit Report

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-04-03c_00 | BEAM Plus EDC submission template for EU-04-03 |  |  |
| EU-04-03c_01 | An energy audit report endorsed by REA |  |  |
| EU-04-03c_02 | Completed Template 1 on Additional Information to Executive Summary of Energy Audit Report and submission record to EMSD |  |  |
| EU-04-03c_03 | Calculation and/or measured data as supporting to the data filled in the template 1 |  |  |

- Carbon Audit Report

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| EU-04-03d_00 | BEAM Plus EDC submission template for EU-04-03 |  |  |
| EU-04-03d_01 | A carbon audit or GHG emission audit report endorsed by a QSP |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)