| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC (including DC with centralised/ shared tank that is outside the assessment boundary) |
| --- | --- |

| Objective | To reduce the water wastage during the maintenance or cleaning of the water tanks and provide an uninterrupted potable and flush water supply to building users. |
| --- | --- |

| Credit Requirement | 1 Bonus credit point for providing twin tank for either potable or flushing water supply system. 2 Bonus credit points for providing twin tank for both potable and flushing water supply system. |
| --- | --- |

| Credit(s) Attainable | 2 Bonus |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

Please confirm that the following requirements are met by checking the box with .

| Twin tanks are installed for potable and flushing supply water systems for all buildings in the assessment boundary |  |
| --- | --- |
| Each compartment of the twin-tank shall be equipped with: - A duplicated set of inlet, outlet and associated overflow and drainage pipeworks - A stop valve at the inlet of each tank compartment to ensure that water will not get into the compartment when it is being cleaned; and - An automatic pump control switch at the downstream side of each sump pump to protect the up-feed system particularly when the stop valve for the tank compartment is closed. |  |

SUBMITTALS

| Supporting Documents. |  | PA | FA |
| --- | --- | --- | --- |
| WU-01-05_00 | BEAM Plus EDC submission template for WU-01-05 |  |  |
| WU-01-05_01 | Plumbing schematic drawing(s) and plumbing layout drawings, highlighting the provisions of the twin tank system for potable water and flush water systems, and the associated installations as stated in items (1) to (3) in the assessment criteria. |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)