| Project Name: |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Project Code: |  |  |  |  |
|  |  | CIR Applied |  | Y |  | N |
|  |  | CIR Number |  |  |  |  |

| Extent of Application | All DC |
| --- | --- |

| Objective | Ensure the DC building are in comfortable acoustic environment. |
| --- | --- |

| Credit Requirement | (a) Background Noise in Data Hall 1 credit point for demonstrating the internal noise level at data hall area are maintained at an appropriate level. (b) Room Acoustics 1 credit point for demonstrating that the mid-frequency reverberation time in applicable rooms meets the prescribed criteria of different types of premises. (c) Noise Isolation 1 credit point for demonstrating airborne noise isolation between rooms, spaces and premises fulfils the prescribed criteria. |
| --- | --- |

| Credit(s) Attainable | 3 |
| --- | --- |
| Credit(s) anticipated for this submission: |  |

COMPLIANCE

- Background Noise in Data Hall

1) Please fill in the blanks and confirm that the following requirement is met by checking the box with .

| Data hall | Space (m2) | Sampling point locations | Methodology adopted |  | Internal noise level, dB (A) | Compliance, i.e. 5 dB(A) better than First Action Level a daily personal noise exposure (LEP, d) of 85 dB(A). |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculations | Measurements |  |  |

- Room Acoustics

1) Please fill in the blanks and confirm that the following requirement is met by checking the box with .

| Type of Premises | Locations | Total Area of relevant space type (m2) | Methodology adopted |  | Compliance |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculations | Measurements | Mid frequencies |  |  |
|  |  |  |  |  | 500hz | 1 kHz | 2 kHz |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |
| Office type premises |  |  |  |  |  |  |  |

- Noise Isolation

1) Please fill in the blanks and confirm that the following requirement is met by checking the box with .

| Type of Premises | Locations | Total Area of relevant space type (m2) | Methodology adopted |  | Compliance |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculations | Measurements | Weighted SRI |  | Level Difference |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |
| Between offices/ conference rooms |  |  |  |  | Rw 44 |  | DnT,w 38 |  |

SUBMITTALS

- Background Noise in Data Hall

| Supporting Documents. |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-03a_00 | BEAM Plus EDC submission template for HWB-03-03 |  |  |
| HWB-03-03a_01 | Endorsed Data hall noise measurement report at representative locations with supporting documents including noise data of the installed IT equipment and Building Service Equipment in data hall |  |  |
| HWB-03-03a_02 | Data hall noise measurement protocol |  |  |
| HWB-03-03a_03 | CV of the professional as per requirements in the assessment |  |  |

- Room Acoustics

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-03b_00 | BEAM Plus EDC submission template for HWB-03-03 |  |  |
| HWB-03-03b_01 | Endorsed Reverberation time measurement or calculation at representative locations with supporting documents of the absorption coefficients |  |  |
| HWB-03-03b_02 | CV of the professional as per requirements in the assessment |  |  |

- Noise Isolation

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-03c_00 | BEAM Plus EDC submission template for HWB-03-03 |  |  |
| HWB-03-03c_01 | Layout plan/ elevation drawings showing the location of the partition walls |  |  |
| HWB-03-03c_02 | Construction details of the partition walls |  |  |
| HWB-03-03c_03 | Endorsed Calculations/ Computer simulation results/ Field test measurement report endorsed by a Corporate Member of Hong Kong Institute of Acoustics or equivalent |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)