| Project Name: |  |  |  | PA submission |  | FA submission |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Project Code: |  |  |  |  |
|  |  |  | CIR Applied |  | Y |  | N |
|  |  |  | CIR Number |  |  |  |  |
| Extent of Application: | All DC |  |  |  |  |  |  |
| Objectives: | To ensure the specified thermal comfort conditions can be achieved under conditions of normal occupancy. |  |  |  |  |  |  |
| Credit Requirement: | - Temperature Profile in Data Hall 1 credit point for sustaining the air temperature at the design value within ±2.0°C when the air side system is operating at steady state under normal operation periods. - Thermal Comfort in Normally Occupied Spaces 1 credit point for demonstrating an appropriate temperature (i.e. ≤25.5°C), relative humidity (i.e. ≤70%) and air velocity (≤0.3 m/s) in normally occupied spaces. |  |  |  |  |  |  |
| Credit(s) Attainable: |  | 2 |  |  |  |  |  |
| Credit(s) anticipated for this submission: |  |  |  |  |  |  |  |
| COMPLIANCE Please check the following boxes and select the appropriate boxes with : Indoor Air Quality Certificate Issuing Bodies (CIB) is employed Please provide Information of the CIB as the following:. Sustained the air temperature at the design value within ±1.5°C when the air side system is operating at steady state under normal operation periods.. Maintained Appropriate temperature (i.e. <25.5°C), relative humidity (i.e. <70%) and air velocity (<0.3 m/s) in normally occupied area.. |

SUBMITTALS

| Supporting Documents |  | PA | FA |
| --- | --- | --- | --- |
| HWB-03-06_00 | BEAM Plus EDC submission template for HWB-03-06 |  |  |
| HWB-03-06_01 | Measurement report endorsed by a CIB |  |  |
| HWB-03-06_02 | Drawings showing the location of measurement locations and ventilation system layouts |  |  |

SPECIAL CIRCUMSTANCE

Describe the circumstance limiting the project team’s ability to complete this form or provide the submittals required in this template. Be sure to reference what additional documentation has been provided, if any. Non-standard documentation will be considered upon its merits (Optional)