## Summary
BEAM Plus Existing Buildings (Version 2.0) Credit Summary Selective Scheme - Energy Use (EU)
BEAM Plus Project No:
Project Name:
1. | Project Description:
2. | Credit Summary
| Section | Credit Requirement | Exclusions | Credit Attainable | Credit Applicable | Credit Anticipated
|  |  |  | 51+2B | Y/N?
EU 1 | Energy Management | a) Energy Management Plan 1 credit for providing an endorsed energy management policy. | None. | 1 | Y
|  | 1 credit for providing energy management plan with objective and targets. |  | 1 | Y
|  | 1 credit for demonstrating that the plan is endorsed by top management of Building Owner/ Building Management Company. |  | 1 | Y
|  | b) Appointment of Energy Warden 1 credit for appointing an Energy Warden in the Building Management Company. |  | 1 | Y
EU 2 | Energy Analysis | a) Data Collection Facilities Maximum 3 credits for providing sub-metering systems for each of the following electrical loads where applicable: i. Chiller plant/ chiller plant with cooling tower (if any); ii. Air-conditioning units; iii. Lighting and small power; and iv. Lift & escalator (if any). | Building to compulsorily comply with BEC 2012 or later version | 3 | Y
|  | b) Data Collection Record 1 credit for providing total building energy consumption data record of at least 2 years for building services under the control of Building Owner/ Building Management Company. | None. | 1 | Y
|  | c) Energy Audit Report 1 credit for conducting energy audit in accordance with the Buildings Energy Efficiency Ordinance (Cap 610) requirement for existing buildings. | None. | 1 | Y
|  | 1 credit for filling up Table (II) to Table (VIII) under the Template 1 on Additional Information to Executive Summary of Energy Audit Report. |  | 1 | Y
|  | d) Carbon Audit Report 1 credit for conducting carbon audit in accordance with the requirements as stipulated in the guideline issued by the Authority. | None. | 1 | Y
EU 3 | Energy Efficient Practices and Measures | a) Energy Efficient Practices Maximum 5 credits for implementing the following energy saving practices: i. Turn on equipment/ systems based on operational hours of buildings. (Operation schedule); ii. Avoid pre-cooling. Switch on centralised A/C system not more than 30 minutes in advance in the morning. (Operation schedules of AC and building); iii. For premises where the A/C systems are provided with heaters, avoid operating the heaters when the outdoor air temperature is above 20°C. (Operation schedule and/or print screen of BMS showing temperature setting); iv. Turn off lighting if it is not needed. (Operation schedule and/or photograph showing timer setting); v. Cut down number of lamps/ luminaires in area over-lit (over CIBSE recommendation) by artificial lighting and in perimeter area sufficiently lit by natural daylight. (Photographs showing lux measurement and de-lamping); vi. Encourage using the stairs (for one or two floors up or down) rather than taking the lift. (Site photograph showing notice/ poster to encourage tenant/ building user); vii. Shut down some of the lifts and escalators during non-peak hours. (Operation schedule); and viii. Arrange routine cleaning schedule for light diffusers, globes and reflectors to ensure light output efficiency (Cleaning schedule). | None. | 5 | Y
|  | b) Energy Efficient Measures Maximum 20 credits for demonstrating the following upgrades in the past 3 years: i. 8 credits for replacing at least 30% by total cooling capacity serving the building from air-cooled chiller to either water-cooled chiller or oil free variable speed air/ water cooled chiller; ii. 6 credits for at least 50% by total cooling capacity serving the building are high efficiency chiller (>15% higher than BEC 2012’s COP at full load in the same category); iii. 6 credits for at least 80% by total cooling capacity of all VRF are high efficiency VRF (>15% higher than BEC 2012’s COP at full load in the same category); iv. 4 credits for at least 50% of total fresh air flow rate to the building are controlled by CO2 sensors; v. 3 credits for at least 50% of air-conditioned areas not frequently used (e.g. meeting room, conference room, etc.) are served by air-conditioning with motion sensors controlling its operation; vi. 4 credits for at least 30% of total fresh air flow rate to the building are pre-treated by heat recovery system; vii. 4 credits for at least 30% of air-conditioned areas are served by enthalpy controlled free cooling; viii. 4 credits for at least 50% of total supply air flow rate of all PAU/ AHU are supplied by VSD fans; ix. 4 credits for at least 50% of total supply air flow rate of all FCU are supplied by VSD fans; x. 4 credits for at least 50% of total chilled water flow rate of all chilled water pumps are VSD driven; | None. | 20 | Y
xi. 4 credits for at least 50% of total condensing water flow rate of all condensing water pumps are VSD driven; xii. 3 credits for having "automatic tube cleaning systems" on all water-cooled chillers; xiii. 4 credits for electronic ballasts for all fluorescent lamps; xiv. 4 credits for replacing >80% of T8 to T5; xv. 4 credits for at least 30% of all areas are served by LED lighting; xvi. 3 credits for at least 30% of all public areas such as corridors, toilets, etc. are served by lighting with motion/ occupancy sensor controls; xvii. 3 credits for at least 30% of all areas accessible to daylight are served by lighting with dimming controls to adjust lighting level to suit the space's need; xviii. 2 credits for having separate lighting controls for the window perimeter and that for the interior. Lighting at the window perimeter can be turned down or off on a sunny day; xix. 5 credits for at least 50% of all window areas with direct access to daylight are applied with solar window film (i.e. windows that are heavily shaded or not having a direct view to the sky are excluded); xx. 3 credits for at least 30% of all lift motor power are re-generative lift;
xxi. 1 credit for at least 30% of all lift motor power are Variable Voltage Variable Frequency (VVVF) drives and/or direct current motor controlled by solid-state elements for lifts; xxii. 1 credit for at least 30% of all escalator motor power are VVVF drive systems and high gear systems for escalators; xxiii. 1 credit for at least 30% of all escalator motor power are controlled by optical sensors to allow escalators to be stopped or slowed down when there are no users; xxiv. 1 credit for at least 50% of all lift (by quantity) have automatic switch off lighting and ventilation fan inside the lift car when the lift is in standby/ idle mode; xxv. 2 credits for adding harmonics filter to reduce total harmonics distortion (THD) in electricity distribution system; xxvi. 1 credit for having heat pump pre-heating at least 50% of domestic hot water (by quantity of sanitary fitting); xxvii. 1 credit for having thermostat on/off and/or speed control for exhaust fans serving at least 50% of plant rooms area but exclude those rooms that require continuous exhaust due to health and safety issues (e.g. chemical storage room, refuse storage room); and xxviii. 1 credit for openable windows for mixed mode/ natural ventilation.
EU 4 | Energy Benchmarking | a) Benchmarking For All types of Buildings: Credit(s) can be achieved based on the benchmarking results obtained from EMSD Benchmarking Tool. Percentile: 50th (1), 40th (3), 30th (5) Alternative for Commercial Buildings: Credit(s) can be achieved based on the label obtained from HKGBC Benchmarking & Energy Saving Tool – Office Buildings (HK BESTOF) . HK BESTOF: Green(1), Bronze(2), Silver or above(3) | None. | 3 | Y
|  | b) Self-Improvement Credits can be achieved based on the reduction percentage by comparing electricity bill/ metering data in the category determined in part a) Benchmarking. (Baseline year can be any year in the past 5 years). i. For buildings ranked at the 40th percentile or below under EMSD Benchmarking Tool/ ”Bronze” or below label obtained from HK BESTOF: Annual energy use reduction: 2%(2), 3%(3), 4%(4), 5%(5), 6%(6), 7%(7), 8%(8) ii. For buildings ranked at the 30th percentile or above under EMSD Benchmarking Tool or “Silver”/ “Gold”/ “Platinum” label obtained from HK BESTOF: Annual energy use reduction: 1%(2), 1.5%(3), 2%(4), 2.5%(5), 3%(6), 3.5%(7), 4%(8) | None. | 8 | Y
EU 5 | Achievement of Energywi$e and Carbon Reduction Certificate | Maximum 2 credits for obtaining the following valid Environmental Certificate of Hong Kong Green Organisation Certification (HKGOC): i. Energywi$e Certificate; and ii. Carbon Reduction Certificate. | None. | 2 | Y
EU 6 | Educational and Promotional Programme | 2 credits for Building Owner/ Building Management Company to educate and advocate the behavioural change of building users in respect of Energy Use by: i. Organising educational seminar/ promotion campaign; or ii. Promoting or participating in Hong Kong Green Building Week organised by Construction Industry Council (CIC) and the Hong Kong Green Building Council Limited (HKGBC). | None. | 2 | Y
EU 7 | Innovative Techniques/ Performance Enhancements | a) Innovative Techniques 1 Bonus credit for applying innovation technique in respect of Energy Use that will improve the performance of the building. | None. | 1B | Y |  | B
|  | b) Performance Enhancements 1 Bonus credit for building with exemplary performance over and above the criteria identified in Energy Use of the BEAM Plus for Existing Buildings. |  | 1B | Y |  | B
Credit Applicable: |  |  |  |  | 51+2B
Credit Anticipated: |  |  |  |  | 0
Percentage of credits achieved: |  |  |  |  | 0%
Grade: |  |  |  |  | Unsatisfactory